Fire Marshal Division

August 10, 2021

Ramona Williams

Re: Miracle Tabernacle Childcare

2301 Ray Rd.

Spring Lake, NC 28390

Application Numbers – BCOM2108-0001

Mrs. Williams

Thank you for submitting the plans for Miracle Tabernacle Childcare Center. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

# 1003.2.11 Means of egress illumination.

  - The means of egress, including the exit discharge, shall be illuminated at all times the building space served by the means of egress is occupied

  - The portion of the exterior exit discharge immediately adjacent to exit discharge doorways in buildings required to have two or more exits.

- 906.1 Fire Extinguishers

  - Fire extinguishers shall be located as not to exceed 75’ of travel distance to an extinguisher.

  - The fire extinguishers provided shall have a minimum rating of 2A10:BC and shall not be installed higher than 5 feet above the finished floor.

Bottom of Form

- 404.2 Fire Safety and Evacuation Plans

  - An approved fire safety and evacuation plan shall be prepared, posted and maintained for Group E occupancies.

- Fire Department Access

  - The fire department access shall extend to within 150 feet of all portions of the facility.

  - The fire department access road shall be of an unobstructed width of not less than 20 feet and shall have an unobstructed vertical clearance of not less the 13 feet 6 inches.

- Fire Alarm System

  - Fire alarm plans shall be submitted for review and approval.

  - The fire alarm system plans shall bear the seal of a licensed P.E. within the state of North Carolina.

    - Spec Sheets shall be submitted for all fire alarm system devices.

    - Any changes to the fire alarm system shall bear the seal of approval of a P.E.

    - Pull stations required at exits from nursery.

- Notes

- Please schedule all fire inspections with the Fire Marshal’s Office.

- 910-893-0740

Thank you again for submitting the plans.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Leslie Jackson

Chief Deputy Fire Marshal