Fire Marshal Division

December 19, 2023

ADT Commercial

Jacob Doyle

3821 Powhatan Rd

Clayton, NC 27520

Re:	Highland Elem.

1915 Buffalo Lake Rd.

Sanford, NC 27332

Application Number – BCOM2112-0003

To Whom It May Concern,

Thank you for submitting the plans for the BDA system. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the facility can be given.  These items are outlined and described below.

- System Design

  - Provide specifications, cut sheets and information on all appliances, devices and wiring to be installed for the BDA system.

  - Plans do not indicate signal strengths from test on page ERRC02.

- BDA System Notes:

- All items in notes are to be completed at the time of final.

- Provide a record of completion of all testing.

- The Fire marshal’s office will witness an acceptance test at completion of project.

- Provide a copy of account history after the acceptance test is completed and approved.

- All work/installation shall be compliant with the 2018 NC Fire Code (Section 510), NFPA 1221 and associated standards as set forth in the NC Fire Code.

- Call Fire Marshal’s office to schedule the BDA acceptance test. (910-893-0740)

Thank you again for submitting the plans for the BDA system.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Leslie Jackson

Leslie Jackson

Chief Deputy Fire Marshal