Fire Marshal Division

January 5, 2022

RLC Construction Company, Inc.

1701 Hobson Road

Dunn, NC 28334

Re: 	J & L Manufacturing

252 Jarco Drive

Fuquay Varina, NC  27521

Application Number BCOM 2112-0005

To whom it may concern,

Thank you for submitting the plans for the J&L Manufacturing project. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

Plan Review Notes

- 906.1  Fire Extinguishers

- All fire extinguishers shall be properly mounted and tagged by a fire extinguisher company.

- Fire extinguishers shall be placed not to exceed 75’ distance of travel.

- The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than 5 feet above the finished floor.

- 506.1  Knox Box

- The installation of a Knox box key box is required and can be ordered on line by clicking the link below.

- https://www.knoxbox.com/store/Knox-Box-3200-Series.cfm

- 505.1  Address Numbers

- Install physical address numbers on the building.

- The numbers are to be visible from the street 6” minimum height required.

Notes:

- Fire Final Inspection required.

*Please schedule all fire inspections with the Fire Marshal’s office*

910-893-0745

Thank you again for submitting the plans for the J&L Manufacturing project. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal