Fire Marshal Division

March 23, 2022

Mr. Brett Strickland

228 Airport Road

Erwin, N.C.  28339

Re:	Campbell University Convocation Office Upfit

56 Main Street

Lillington, NC 27546

Application Number BCOM2203-0010

Mr. Strickland,

Thank you for submitting the plans for the office upfit. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the facility can be given.  These items are outlined and described below.

- State of Compliance.

  - Before requesting final approval of the installation, where required by the fire code official, the installing contactor shall furnish a written statement to the fire code official that the subject fire protection system has been installed/re-located in accordance with the manufacture’s specifications and the appropriate installation standard. Any deviations from the design standards shall be noted and copies of the approvals for such deviations shall be attached to the written statement.

  - All work shall be performed in accordance with NFPA 13, NFPA 72 and the 2018 North Carolina State Fire Code.

- Fire Extinguishers

  - Minimum of (1) 2A10:BC fire extinguisher shall be installed not to exceed 75’ distance of travel.

  - All Fire extinguishers shall be properly mounted and tagged by a fire extinguisher company.

- Means of Egress Illumination

- The means of egress, including the exit discharge, shall be illuminated at all time the building space is served by the means of egress is occupied.

- Means of egress consist of three separate and distinct parts: the exit access, the exit and the exit discharge.

- The means of egress illumination shall not be less than 1 foot-candle at the walking surface.

- Relocate exit sign over receptionist door to the end of hallway next to the new directors office, directly egress towards the rear exit.

- Penetrations

  - All penetrations in fire rated construction must be UL listed and inspected.

- Fire Protection Systems

- Any new fire protection devices added shall be compatible with existing fire sprinkler and alarm system.

- All equipment and work shall be conducted per NFPA 72 and NFPA 13.

- A certification of completion, from the alarm company and an acceptance test shall be provide at final inspection.

- Notes

- All additions to existing systems shall properly communicate to existing fire panel.

- A fire alarm and fire sprinkler system construction permit is required.

- Please schedule all inspections through the Fire Marshal’s Office.

910-893-0742.

Thank you again for submitting the plans for the office upfit.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal