## Calculator
version 1.059 (9/15/2011)
Honeywell Security | Facility Information | [5 empty] | Enter Standby and Alarm Times |  |  | Battery Contigency Factor
Battery & Power Budget Calculator | Location: | Potters Vessel Church |  |  |  |  | Battery Standby (hours): |  | 24
© 2003 Honeywell International Inc. All Rights Reserved | Account #: | Dynamark 1171551 |  |  |  |  | Alarm Duration (minutes): |  | 5
| Model: | Vista 32 FBP
| Engineer: | Curtiss Shirley | [5 empty] | Recommended | 8.613
| Date: | 2022-10-03 | [5 empty] | Battery (AH)
[7 empty] | Recommended Battery Capacity OK for 48-Hr Recharge |  |  |  |  | TRUE | FALSE |  | FALSE
| SELECTED PANEL MAXIMUM OUTPUT RATINGS | [10 empty] | 1
Select Panel from pulldown list: | Polling Loop (mA) | Standby Auxiliary Power (mA) | Alarm Auxiliary Power (mA) | Panel Standby (mA) | Panel Alarm (mA) | Bell #1 Output (mA) | Bell #2 Output (if used; mA) | Maximum Panel Standby Output | Maximum Panel Alarm Output | Max Battery Supported by Panel | All Keypads? | SN Vplex? | AUI Support? | Commercial Fire Rated | Polling Loop Support
| 128 | 750 | 1000 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 34.4 | 0 | 1 | 0 | 1 | 1
[8 empty] | Total Standby | Total Alarm
Calculated Current Draw | 0 | 3 | 20 |  | Calculated Bell Draw | 814 | 672 | 3 | 1506
[8 empty] | Standby Budget | Alarm Budget
Power Budget | 128 | 747 | 980 |  | Bell Power Budget | 886 | 1028 | 1297 | 1294
| Current OK | Current OK | Current OK |  |  | Current OK |  | Current OK | Current OK
[5 empty] | External Bell Power Req'd (mA): | 0 |  |  | Ext. UL Power Req'd (mA): | 130
TRUE
Grayed-out device(s) are not supported by selected panel
KEYPADS/INTERFACES | Enter Quantity | How many powered externally? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Alarm Current | Total External Current Required | Modifiers (LEDs, etc.)
6128 | 0 | 0 | 30 | 45 |  |  | 0 | 0 | 0
6128RF | 0 | 0 | 60 | 120 |  |  | 0 | 0 | 0 | FALSE
6137 | 0 | 0 | 40 | 85 |  |  | 0 | 0 | 0
6139/6139R | 0 | 0 | 40 | 100 |  |  | 0 | 0 | 0
6148 | 0 | 0 | 30 | 55 |  |  | 0 | 0 | 0
6149EX | 0 | 0 | 40 | 60 |  |  | 0 | 0 | 0
6150 | 0 | 0 | 40 | 70 |  |  | 0 | 0 | 0
6150RF | 0 | 0 | 80 | 105 |  |  | 0 | 0 | 0
6150V | 0 | 0 | 60 | 160 |  |  | 0 | 0 | 0
6150RF | 0 | 0 | 80 | 105 |  |  | 0 | 0 | 0
6160/6160CR | 1 | 0 | 45 | 150 |  |  | 45 | 150 | 0
6160CR-2 | 0 | 0 | 45 | 160 |  |  | 0 | 0 | 0
6160PX | 0 | 0 | 40 | 165 |  |  | 0 | 0 | 0
6160RF | 0 | 0 | 50 | 150 |  |  | 0 | 0 | 0
6160V | 0 | 0 | 60 | 190 |  |  | 0 | 0 | 0
6164US | 0 | 0 | 55 | 210 |  |  | 0 | 0 | 0 | FALSE
6165EX | 0 | 0 | 40 | 70 |  |  | 0 | 0 | 0
6270 | 0 | 0 | 180 | 280 |  |  | 0 | 0 | 0
6271C | 0 | 0 | 159 | 230 |  |  | 0 | 0 | 0
6271CV | 0 | 0 | 159 | 230 |  |  | 0 | 0 | 0
6271V | 0 | 0 | 137 | 210 |  |  | 0 | 0 | 0
6272CV | 0 | 0 | 180 | 305 |  |  | 0 | 0 | 0
6272CSV | 0 | 0 | 180 | 305 |  |  | 0 | 0 | 0
6272CBV | 0 | 0 | 180 | 305 |  |  | 0 | 0 | 0
6460S | 0 | 0 | 40 | 150 |  |  | 0 | 0 | 0
6460W | 0 | 0 | 40 | 150 |  |  | 0 | 0 | 0
8132iPK (Symphony) | 0 | 0 | 350 | 400 |  |  | 0 | 0 | 0
FSA-8 Fire Zone Annunciator | 0 | 0 | 35 | 65 |  |  | 0 | 0 | 0
FSA-24 Fire Zone Annunciator | 0 | 0 | 35 | 130 |  |  | 0 | 0 | 0
Add'l Keypd (Enter # and Currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Add'l Keypd (Enter # and Currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
| Power Overdraw if highlighted | [5 empty] | Panel Max Output Exceeded if highlighted
2 WIRE & 4 WIRE SMOKE DETECTORS (except Vplex Polling Loop detectors) | Enter Quantity | How many powered externally? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Alarm Current | Total External Current Required
2 wire smoke detector (zone powered) | 1 |  | Two-wire smoke detector current is built into the panel budgets. These fields are included to help you create a complete equipment list. The line below indicates if number of detectors exceeds panel capacity, or if the selected panel does not support 2-wire smoke detectors.
4 wire duvt detectors | 0
2 wire smoke detector (zone powered) | 0
2 wire smoke detector (zone powered) | 0 |  | Quantity of 2 Wire Smoke Detectors OK for selected panel! | [7 empty] | -31
4 Wire duct detector | 0 | 2 | 21 | 65 |  |  | -42 | -130 | 130
12V 4 wire Smoke ( Qnt'y & Currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
12V 4 wire Smoke ( Qnt'y & Currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
12V 4 wire Smoke ( Qnt'y & Currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
MULTI-POWER DEVICES | Enter Quantity | How many powered externally? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Alarm Current | Total External Current Required
4208U [powered by polling loop] | 0 | 0 | 0 | 0 | 27.3 | 0 | 0 | 0 | 0 |  | FALSE
4208U [powered by panel aux power] | 0 | 0 | 28 | 0 | 0.6 | 0 | 0 | 0 | 0 |  | TRUE
4208U [powered externally] | 0 | 0 | 28 | 0 | 0.6 | 0 | 0 | 0 | 0 |  | TRUE
4208SN [powered by polling loop] | 0 | 0 | 0 | 0 | 33.6 | 0 | 0 | 0 | 0 |  | FALSE
4208SN [powered by panel aux power] | 0 | 0 | 33 | 0 | 0.6 | 0 | 0 | 0 | 0 |  | FALSE
4208SN [powered externally] | 0 | 0 | 33 | 0 | 0.6 | 0 | 0 | 0 | 0 |  | FALSE
4208SNF [powered by polling loop] | 0 | 0 | 0 | 0 | 33.6 | 0 | 0 | 0 | 0 |  | FALSE
4208SNF [powered by panel aux power] | 0 | 0 | 40 | 0 | 0.6 | 0 | 0 | 0 | 0 |  | FALSE
4208SNF [powered externally] | 0 | 0 | 40 | 0 | 0.6 | 0 | 0 | 0 | 0 |  | FALSE
4208SNF (Class B to A Zone Converter) | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0
4209U Grouped Zone Mux. Module | 0 | 0 | 110 | 0 | 15.5 | 0 | 0 | 0 | 0
4209U [powered externally] | 0 | 0 | 110 | 0 | 15.5 | 0 | 0 | 0 | 0
4297 Polling Loop Extender | 0 | 0 | 178 | 0 |  | 0 | 0 | 0 | 0
Add'l Device (enter quant. & currents) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Add'l Device (enter quant. & currents) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Power Overdraw if highlighted | [5 empty] | Panel Max Output Exceeded if highlighted
AUXILIARY POWERED DEVICES | Enter Quantity | How many powered externally? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Alarm Current | Total External Current Required
PS24 24 volt Power Supply Module | 0 | 0 | 50 | 100 |  |  | 0 | 0 | 0
4100SM (no more than one per system) | 0 | 0 | 25 | 0 |  |  | 0 | 0 | 0
4204: Enter no. of relays used | 0 | 0 | 40 | 0 |  |  | 0 | 0 | 0
4204CF:Enter no. of relays used | 0 | 0 | 80 |  |  |  | 0 | 0 | 0
4285 Voice Module | 0 | 0 | 160 |  |  |  | 0 | 0 | 0
4286 with warning speakers | 0 | 0 | 220 | 300 |  |  | 0 | 0 | 0
5140DLM Backup Dialer Module | 0 | 0 | 5 | 15 |  |  | 0 | 0 | 0
5800RP wireless repeater module | 0 | 0 | 100 |  |  |  | 0 | 0 | 0
5800TM wireless xmtr module | 0 | 0 | 20 |  |  |  | 0 | 0 | 0
5881EN receiver | 0 | 0 | 60 |  |  |  | 0 | 0 | 0
5883 hi-security receiver | 0 | 0 | 80 |  |  |  | 0 | 0 | 0
UVS-QM | 0 | 0 | 75 | 110 |  |  | 0 | 0 | 0
VA8200 Panel Linking Module | 0 | 0 | 88 | 0 |  |  | 0 | 0 | 0
VA8201 Alpha Pager Module | 0 | 0 | 165 | 0 |  |  | 0 | 0 | 0
Add'l Device (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Add'l Device (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Communicators
7845GSM/7845i-GSM | 0 | 0 | 10 |  |  |  | 0 | 0 | 0 | FALSE
7845i/7845i-ENT | 0 | 0 | 10 |  |  |  | 0 | 0 | 0 | TRUE
GSMCF/iGSMCF Fire Communicator | 0 | 0 | 10 |  |  |  | 0 | 0 | 0 | FALSE
Vista-GSM/Vista-GSMCN (Vista-21iP only) | 0 | 0 | 10 |  |  |  | 0 | 0 | 0 | FALSE
7847i/7847i-E Internet Communicator | 0 | 0 | 75 |  |  |  | 0 | 0 | 0
Add'l Device (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Add'l Device (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
PIR Motion Detectors (non Vplex)
IS215T | 0 | 0 | 7 |  |  |  | 0 | 0 | 0 | FALSE
IS215TCE | 0 | 0 | 18 |  |  |  | 0 | 0 | 0
IS2260/IS2260T | 0 | 0 | 4 |  |  |  | 0 | 0 | 0 | FALSE
IS2460 | 0 | 0 | 9 |  |  |  | 0 | 0 | 0
IS2500LT | 0 | 0 | 25 |  |  |  | 0 | 0 | 0
IS2535/IS2535T | 0 | 0 | 20 |  |  |  | 0 | 0 | 0
IS2560/IS2560T | 0 | 0 | 20 |  |  |  | 0 | 0 | 0
IS2560TC | 0 | 0 | 25 |  |  |  | 0 | 0 | 0
IS310/IS320 Request to Exit (RTE) | 0 | 0 | 35 |  |  |  | 0 | 0 | 0
997 Ceiling Mount PIR | 0 | 0 | 12 |  |  |  | 0 | 0 | 0 | FALSE
998 Wall Mount PIR | 0 | 0 | 18 |  |  |  | 0 | 0 | 0 | TRUE
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Dual Tech Motion Detectors (non Vplex)
DT-515 | 0 | 0 | 20 | 0 |  |  | 0 | 0 | 0
DT-6100STC | 0 | 0 | 35 | 0 |  |  | 0 | 0 | 0
DT-7235T | 0 | 0 | 20 | 0 |  |  | 0 | 0 | 0
DT-7435/DT-7435C | 0 | 0 | 30 | 0 |  |  | 0 | 0 | 0
DT-7450/DT-7450MIC | 0 | 0 | 35 | 0 |  |  | 0 | 0 | 0
DT-7550 | 0 | 0 | 40 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Motion Detctrs (enter quant. & currents) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
| Power Overdraw if highlighted | [5 empty] | Panel Max Output Exceeded if highlighted
grayed-out devices are not supported by selected panel
POLLING LOOP DEVICES | Enter Quantity | How many powered by 4297? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Alarm Current | Total External Current Required | Modifiers (LEDs, etc.)
4101SN Single Output Relay Module | 0 | 0 |  |  | 7 | 0
4190SN Two Zone SIM | 0 | 0 |  |  | 2 | 0
4190WH | 0 | 0 |  |  | 2 | 0
4191SN-WH | 0 | 0 |  |  | 0.5 | 0
4192CP | 0 | 0 |  |  | 0.4 | 0
4192SD Photoelectric Smoke Det. | 0 | 0 |  |  | 0.4 | 0
4192SDT | 0 | 0 |  |  | 0.4 | 0
4193SN Two Zone SIM | 0 | 0 |  |  | 1.5 | 0
4194 Contact | 0 | 0 |  |  | 1 | 0
4196 | 0 | 0 |  |  | 1 | 0
4209U | 0 | 0 |  |  | 15.5 | 0
4275EX Dual PIR | 0 | 0 |  |  | 1 | 0 |  |  |  | FALSE
4275EX-SN Dual PIR | 0 | 0 |  |  | 1 | 0 |  |  |  | FALSE
4278EX-SN | 0 | 0 |  |  | 1 | 0 |  |  |  | FALSE
DT7500SN | 0 | 0 |  |  | 2.6 | 0 |  |  |  | FALSE
4293SN | 0 | 0 |  |  | 1 | 0
4939SN WH/BR/GY Surf Mt. Cntct. | 0 | 0 |  |  | 1 | 0
4944SN Recessed Contact | 0 | 0 |  |  | 1 | 0
4945SN-WH | 0 | 0 |  |  | 0.5 | 0
4959SN Overhead Door Contact | 0 | 0 |  |  | 0.5 | 0
5192SD Smoke Detector | 0 | 0 |  |  | 1.2 | 0 |  |  |  | FALSE
5192SDT Smoke w/ Heat | 0 | 0 |  |  | 1.2 | 0 |  |  |  | FALSE
5193SD Smoke Detector | 0 | 0 |  |  | 1.2 | 0 |  |  |  | FALSE
5193SDT Smoke w/ Heat | 0 | 0 |  |  | 1.2 | 0 |  |  |  | FALSE
998MX PIR | 0 | 0 |  |  | 1 | 0 |  |  |  | FALSE
IS2500SN PIR | 0 | 0 |  |  | 1.6 | 0 |  |  |  | FALSE
FG-1625SN Glass Break Detector | 0 | 0 |  |  | 1 | 0
Quest2260SN | 0 | 0 |  |  | 6 | 0 |  |  |  | FALSE
Vplex-VSI Short Isolator | 0 | 0 |  |  | 5 | 0
Vistakey | 0 | 0 |  |  | 2 | 0
Add'l VPlex (enter qnt'y & current) | 0 | 0 |  |  | 0 | 0
Add'l Vplex (enter qnt'y & current) | 0 | 0 |  |  | 0 | 0
| Polling Loop Overdraw if highlighted! Add 4297 Devices (row 41) | [5 empty] | Panel Max Output Exceeded if highlighted
12V NOTIFICATION DEVICES ON BELL OUTPUT #1 | Enter Quantity | How many powered externally? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Sounder Current from Panel Bell #1 | Total Sounder Current (external)
P2RL Wall Horn Strobe 15/75 CD | 4 | 0 |  | 142 |  |  |  | 568 | 0
P2RL Wall Horn Strobe 30CD | 0 | 0 |  | 158 |  |  |  | 0 | 0
SRL Wall Mount Strobe 15CD | 2 | 0 |  | 123 |  |  |  | 246 | 0
P2R Wall Horn strobe 15/75 CD | 0 | 0 |  | 0 |  |  |  | 0 | 0
Enter device name, quant., & current | 0 | 0 |  | 0 |  |  |  | 0 | 0
| Bell #1 Power Overdraw if highlighed! | [5 empty] | Panel Max Output Exceeded if highlighted
12V NOTIFICATION DEVICES ON BELL OUTPUT #2 (IF USED) | Enter Quantity | How many powered externally? | Standby (aux pwr) | Alarm Current (Aux) | Polling Loop | Total Polling Loop | Total Standby Current | Total Sounder Current from Panel Bell #2 | Total Sounder Current (external)
P2RL Wall Horn Strobe 15/75 CD | 3 | 0 |  | 142 |  |  |  | 426 | 0
P2RL Wall Horn Strobe 15CD | 0 | 0 |  | 98 |  |  |  | 0 | 0
SRL Wall Mount Strobe 15CD | 2 | 0 |  | 123 |  |  |  | 246 | 0
Enter device name, quant., & current | 0 | 0 |  | 0 |  |  |  | 0 | 0
Enter device name, quant., & current | 0 | 0 |  | 0 |  |  |  | 0 | 0
| Bell #2 Power Overdraw if highlighed! | [5 empty] | Panel Max Output Exceeded if highlighted
12V AUX POWER AND BELL CIRCUIT WIRE RUN DATA | Units | Wire Gauge(AWG) |  | Ohms per 1000 ft | Alarm Current Draw (mA) | Run Length | Actual Resistance (twin leads) | Voltage At EOL | Voltage Drop (Percent) |  | Unit Selection
Panel Aux Power Wire Run (twin lead) |  |  |  | 8.08 | 20 | 50 | 0.808 | 11.9838 | 0.13467 |  | 1
Panel Bell 1 Wire Run (twin lead) |  |  |  | 5.08 | 814 | 145 | 1.4732 | 10.8008 | 9.9932 |  | 1
Panel Bell 2 Wire Run (twin lead) |  |  |  | 5.08 | 672 | 170 | 1.7272 | 10.8393 | 9.6723 |  | 1
PS24 Power Supply | [6 empty] | Standby/Alarm Durations (from top)
Battery & Power Budget Calculator | [6 empty] | Battery Standby (hours): |  | 24
© 2003 Honeywell International Inc. All Rights Reserved | [6 empty] | Alarm Duration (minutes): |  | 5
[7 empty] | Required Capacity (AH) |  | 1.0593 |  | 4
[5 empty] | Use TWO identical batteries w/ this AH capacity |  |  |  | 7
7
[7 empty] | Recommended Battery Capacity OK for 48-Hr Recharge |  |  |  |  | FALSE | FALSE |  | FALSE
| PS24 POWER SUPPLY MODULE, MAXIMUM CAPACITIES | [10 empty] | 1
| Panel 12V Standby (mA) | Panel 12V Alarm (mA) | Output A Standby (mA) | Output A Alarm (mA) | Output B Standby (mA) | Output B Alarm (mA) | PS24 PC Board (mA) | Maximum Total Standby Output | Maximum Total Alarm Output | Max. Battery Capacity | Unit Selection
| 303 | 1976 | 570 | 1700 | 570 | 1700 | 40 | 610 | 4180 | 34.4 | FALSE
[8 empty] | Total Standby | Total Alarm
Equivalent panel load @ 24V | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 40
(converted to 12VDC from 24V full-wave) | [7 empty] | Standby Budget | Alarm Budget
Power Budget | 303 | 1976 | 570 | 1700 | 570 | 1700 |  | 570 | 4140 | 34.4
[6 empty] | Current OK | 0 | Current OK | Current OK
24V NOTIFICATION APPLIANCES Enter Device Names & Specifications | Enter Quantity | Which PS24 Output? | Device Standby Load (MA) | Device Alarm Load (MA) |  | Subtotal A Standby | Subtotal A Alarm | Subtotal B Standby | Subtotal B Alarm |  | Output Selection
| 0 | 0 | 0 | 107 |  | 0 | 0 | 0 | 0 | 3 | 1
|  | 0 | 0 | 79 |  | 0 | 0 | 0 | 0 |  | 2
|  | 0 | 0 | 66 |  | 0 | 0 | 0 | 0 |  | 2
HORN/STROBE:SYS-P2R 30 Cdl |  | 0 | 0 | 107 |  | 0 | 0 | 0 | 0 |  | 2
| 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 79 |  | 0 | 0 | 0 | 0 |  | 1
SYS SR 30 CDL | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
SYS SR 30 CDL | 0 | 0 | 0 | 79 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V Notification Appliance | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 1
24V BELL CIRCUIT WIRE RUN DATA | Units | Wire Gauge(AWG) |  | Ohms per 1000 ft | Total Alarm Current Draw (mA) | Run Length | Actual Resistance (twin leads) | Voltage At EOL | Voltage Drop (Percent) |  | Unit Selection
PS24 Output A Wire Run (twin lead) |  |  |  | 5.08 | 0 | 100 | 1.016 | 24 | 0 |  | 1
PS24 Output B Wire Run (twin lead) |  |  |  | 5.08 | 0 | 50 | 0.508 | 24 | 0 |  | 1
Note on A1: Added VISTA-21iP, DT7500SN, 5193SD/SDT
Note on A55: 2 wire smokes are powered by the control panel zone(s), and are included as part of the panel's base current draw. Enter type and quantity here
Note on A56: 2 wire smokes are powered by the control panel zone(s), and are included as part of the panel's base current draw. Enter type and quantity here
Note on A57: 2 wire smokes are powered by the control panel zone(s), and are included as part of the panel's base current draw. Enter type and quantity here
Note on A58: 2 wire smokes are powered by the control panel zone(s), and are included as part of the panel's base current draw. Enter type and quantity here
Note on A59: Enter device type and current draw values here
Note on A60: Enter device type and current draw values here
Note on A61: Enter device type and current draw values here
Note on A62: Enter device type and current draw values here
Note on A103: 7845GSM and 7845i-GSM digital communicators are powered via their own power supply. If installed in ECP mode, the devices draw 10mA from the ECP bus.
Note on A104: 7845iENT digital communicators are powered via their own power supply. If installed in ECP mode, the devices draw 10mA from the ECP bus.
Note on A105: GSMCF digital communicators are powered via their own power supply. If installed in ECP mode, the devices draw 10mA from the ECP bus.
Note on B15: If overdrawn (RED), then add 4297 devices as needed to expand capacity. (4297 devices appear in the MULTI-POWER DEVICES table below) Refer to the panel installation instructions for details.
Note on C3: IMPORTANT! Always check the product documentation to make sure the selected peripherals are compatible with the selected panel. Not all peripherals listed in this tool are compatible with the selected panel! You are required to follow the installation recommendations as listed in the panel and peripheral documentation.
Note on C15: If overdrawn (RED), power some devices from additional UL-listed power supply as needed. Enter quantity of externally powered devices in Column C. Refer to panel instructions for details.
Note on D15: If overdrawn (RED), power some devices from additional UL-listed power supply as needed. Enter quantity of externally powered devices in Column C. Refer to panel instructions for details.
Note on D210: If overdrawn (RED), reconfigure or use external power. Refer to panel and device instructions for details.
Note on E210: If overdrawn (RED), reconfigure or use external power. Refer to panel and device instructions for details.
Note on F210: If overdrawn (RED), reconfigure or use external power. Refer to panel and device instructions for details.
Note on G15: If overdrawn (RED), use UL-listed externally powered bell; refer to panel instructions for details.
Note on G17: If required, add external bell power supply with AT LEAST this capacity.
Note on G210: If overdrawn (RED), reconfigure or use external power. Refer to panel and device instructions for details.
Note on H15: If overdrawn (RED), use UL-listed externally powered bell; refer to panel instructions for details.
Note on I15: If overdrawn (RED), reconfigure some devices using external power. Refer to panel instructions for details.
Note on I210: If overdrawn (RED), reconfigure some devices using external power. Refer to panel instructions for details.
Note on J15: If overdrawn (RED), reconfigure some devices using external power. Refer to panel instructions for details.
Note on J210: If overdrawn (RED), reconfigure some devices using external power. Refer to panel instructions for details.
Note on K2: This value is used to compensate for the way a lead-acid battery changes over time. Typically, for standby times of 4 hours or less, the contingency factor is 40%; for longer standby times (e.g. 24 hours) the contingency factor is 10%. These requirements change locally; check with your AHJ and set this value accordingly.
Note on K17: If required, add external UL-Listed power supply with AT LEAST this capacity.
Note on K210: If overdrawn (RED), power some devices from additional UL-listed power supply as needed. Enter quantity of externally powered devices in Column C. Refer to panel instructions for details.
LED Active?
LED Active?
LED Active?
Using Relay?
LED Active?
LED Active?
Commercial Fire Installation
Commercial Burg Installation
Apply UL Power Limits? (Required to maintain UL Listing including UL864)
LED Active?
Using PS24 to back up Control Panel
Remove Unused Devices From List
LED Active?
LED Active?
LED Active?
LED Active?
Using Relay?
LED Active?
LED Active?
LED Active?
LED Active?
LED Active?

## Data (hidden)
No. | Panel | Polling Loop (mA) | Aux. Power (normal; mA) | Aux. Power (alarm; mA) | Panel Standby (mA) | Panel Alarm (mA) | Bell #1 Output (mA) | Bell #2 Output (mA) | Max Panel Standby Output | Max Panel Alarm Output | Supports Polling Loop? | Supports Graphic UI? | Supports SN Vplex Devices? | Supports All Keypads? | Comm'l Fire Rated? | Max. Batt Capacity (AH) | 2W Smokes? | 2 | Lookup from Select Panel control
1 | <Select Panel> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2 | Vista-32FB | 128 | 750 | 1000 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 0 | 1 | 0 | 1 | 34.4 | 32
3 | 5110XM | 0 | 350 | 1000 | 155 | 235 | 1000 | 0 | 350 | 1000 | 0 | 0 | 0 | 0 | 1 | 14 | 16
4 | 5140XM | 64 | 750 | 750 | 300 | 470 | 1700 | 1700 | 1000 | 2300 | 1 | 0 | 0 | 0 | 1 | 34.4 | 32
5 | Vista-100 | 128 | 1000 | 1700 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 0 | 1 | 0 | 1 | 34.4 | 32
6 | Vista-128B | 128 | 750 | 1000 | 250 | 330 | 1700 | NA | 1000 | 1700 | 1 | 0 | 1 | 0 | 0 | 17.2 | 16
7 | Vista-128BP | 128 | 750 | 1000 | 250 | 330 | 1700 | NA | 1000 | 1700 | 1 | 1 | 1 | 1 | 0 | 17.2 | 16
8 | Vista-128FB | 128 | 1000 | 1700 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 0 | 1 | 0 | 1 | 34.4 | 32
9 | Vista-128FBP | 128 | 1000 | 1700 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 1 | 1 | 0 | 1 | 34.4 | 32
9 | Vista-128FBP (UL864 Edition 9) | 128 | 1000 | 1700 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 1 | 1 | 0 | 1 | 34.4 | 32
11 | Vista-250BP | 128 | 750 | 1000 | 250 | 330 | 1700 | NA | 1000 | 1700 | 1 | 1 | 1 | 1 | 0 | 17.2 | 16
12 | Vista-250FBP | 128 | 1000 | 1700 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 1 | 1 | 0 | 1 | 34.4 | 32
12 | Vista-250FBP (UL864 Edition 9) | 128 | 1000 | 1700 | 300 | 470 | 1700 | 1700 | 1300 | 2800 | 1 | 1 | 1 | 0 | 1 | 34.4 | 32
14 | Vista-40 | 64 | 750 | 750 | 250 | 330 | 1700 | NA | 1000 | 1700 | 1 | 0 | 1 | 1 | 0 | 17.2 | 16
15 | Vista-50P | 64 | 750 | 750 | 250 | 330 | 1700 | NA | 750 | 1700 | 1 | 0 | 1 | 1 | 0 | 34.4 | 16
16 | 7720ULF | 0 | 150 | 600 | 100 | 900 | 500 | NA | 250 | 2100 | 0 | 0 | 0 | 0 | 1 | 7 | 0
17 | 7720ULFPLUS | 0 | 150 | 900 | 100 | 900 | 500 | NA | 250 | 2100 | 0 | 0 | 0 | 0 | 1 | 7 | 0
18 | Vista-21iP | 0 | 600 | 600 | 85 | 160 | 2000 | NA | 600 | 2000 | 0 | 1 | 0 | 1 | 0 | 17.2 | 16
19 | Vista-20PS | 0 | 600 | 600 | 85 | 160 | 2000 | NA | 600 | 2000 | 0 | 1 | 0 | 1 | 0 | 17.2 | 16
20 | Vista-20P | 0 | 600 | 600 | 85 | 160 | 2000 | NA | 600 | 2000 | 0 | 1 | 0 | 1 | 0 | 17.2 | 16
21 | <Select Panel> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Battery Contingency (normally 1.1 (10%), 1.2 (20%), or 1,4 (40%).
This value is carried to Battery Capacity calculation (in cell Calculator!J6), and is used to compensate for the way a lead-acid battery changes over time. Select one of the two methods for calculating this below, and copy the appropriate cell into B20.
Contingency Factor: | 1.1
This code adds a combo-box selector to the Calculator page, which will enable the user to select battery contingency factors of 10%, 20%, or 40%. This code is here in case customer feedback indicates that they want battery contingency as a manual selection. To implement, copy the combo box to the calculator page, and copy cell D26 to B20. | [5 empty] | This code automatically selects battery contingency factor based on standby time (in cell Calculator!J3). Using this method, the factor is 1.4 if standby time is 4 hours or less, and 1.1 (10%) if the standby time is over 4 hours. To implement, copy cell G26 to B20.
Number | Factor | Value | Selection
1 | 10% | 1.1 | 1
2 | 20% | 1.2
3 | 40% | 1.4 | 1.1 |  |  | 1.1
Line Drop Calculations | Gauge | Ohms/1K ft | Ohms/1KM | Lookups from Calc Page |  | Unit Selection | Units | Lookup
1 | <Select Wire Gauge> | 0 | 0 | 8 |  | 1 | Feet | 1 | 2
2 | #12 AWG Solid | 2.01 | 6.5945 | 6 |  | 2 | Meters | 1
3 | #12 AWG Stranded | 2.05 | 6.7257 | 6
4 | #14 AWG Solid | 3.19 | 10.4659 | 6 |  | Output Selection | Output
5 | #14 AWG Stranded | 3.26 | 10.6955 | 6 |  | 1 | Output A
6 | #16 AWG Solid | 5.08 | 16.6667 |  |  | 2 | Output B
7 | #16 AWG Stranded | 5.29 | 17.3556
8 | #18 AWG Solid | 8.08 | 26.5092
9 | #18 AWG Stranded | 8.45 | 27.7231
10 | #20 AWG solid | 10.15 | 33.2
11 | #20 AWG Stranded | 10.5 | 34.1
12 | #22 AWG Solid | 16.14 | 51.7
13 | #22 AWG Stranded | 16.8 | 52.7
Note on O1: Does this panel support fixed glass keypads? 0 is "no support"; 1 is "supports". If a panel does not support fixed glass, items on calculator page are disabled.
Note on P1: Does this panel support fixed glass keypads? 0 is "no support"; 1 is "supports". If a panel does not support fixed glass, items on calculator page are disabled.
Note on S1: this field is driven by panel selection combo box on previous page & is used as lookup ref for this panel data.