Fire Marshal Division

March 13, 2024

Robert J. Bracken

3768 Carbonton Road

Sanford, NC  27330

RE: 	Champs Convenience Store

8920 US 401 North

Fuquay-Varina, NC 27526

To Whom It May Concern,

Thank you for submitting plans for the Champs Convenience Store. The plans have been reviewed by a qualified code enforcement official for compliance with the North Carolina Fire Prevention code and all other fire protection regulations. The following are items that will need to be addressed before a final inspection of this project can be completed. The items are listed and described below.

- Physical Address

- The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

- The numbers used to make up the physical address shall be at least 6 inches in height.

- Knox Box

- Keys for the front entrance door shall be provided in a Knox box for the premises.  The Knox box shall be installed near the front entrance on the outside of the building.  Contact our office for further details.

- Commercial hood and duct systems. (If Required)

  - Each required commercial kitchen exhaust hood and duct system required by Section 609 to have a Type I hood shall be protected with an approved automatic fire-extinguishing system installed in accordance with this code.

      - An additional permit is required for kitchen hood suppression system.

        - Provide fire suppression plans, shop drawings and cut sheets.

- Commercial cooking systems.( If Required)

  - The automatic fire-extinguishing system for commercial cooking systems shall be of a type recognized for protection of commercial cooking equipment and exhaust systems of the type and arrangement protected. Pre-engineered automatic dry- and wet-chemical extinguishing systems shall be tested in accordance with UL 300 and listed and labeled for the intended application. Other types of automatic fire-extinguishing systems shall be listed and labeled for specific use as protection for commercial cooking operations. The system shall be installed in accordance with this code, its listing and the manufacturer’s installation instructions. Automatic fire-extinguishing systems of the following types shall be installed in accordance with the referenced standard indicated, as follows:

1. Carbon dioxide extinguishing systems, NFPA 12.

2. Automatic sprinkler systems, NFPA 13.

3. Foam-water sprinkler system or foam-water spray systems,

NFPA 16.

4. Dry-chemical extinguishing systems, NFPA 17.

5. Wet-chemical extinguishing systems, NFPA 17A.

Exception: Factory-built commercial cooking recirculating systems that are tested in accordance with UL 710B and listed, labeled and installed in accordance with Section 304.1 of the International Mechanical Code.

- Portable fire extinguishers for commercial cooking equipment.

  - Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with the N.C. Fire Code.

- Fire Extinguishers

  - Fire extinguishers shall be placed in approved locations and may be field verified on final inspection. The fire extinguishers provided shall have a minimum rating of 2A 10 B: C. Fire extinguisher shall be installed not to exceed 75’ distance of travel, not noted on the plans.

  - A 2A 10B: C shall be installed not to exceed 75’ distance of travel from motor fuel dispensing equipment, not noted on the plans.

- 3404.2.9.6.5 Vehicle Impact Protection

- Where any portions of the fuel storage or dispensing components are subject to vehicular impact, they shall be protected therefrom, either by having  the impact protection incorporated into the system design in compliance with the impact test protocol  of UL 2085, or by meeting the provisions of Section 312 NCFC , or where necessary, a combination of both. Where guard posts or other approved barriers are provided.

- Fuel Dispensing.

  - An additional permit is required for fuel dispensing operations (piping inspection) and for each tank to be installed.

- Plans shall be submitted for the fuel tanks, fuel piping, and all appurtenances that are associated with the fuel deliver system.  A general site plan detailing the location of the tanks, dispensers, and fuel lines, emergency shut-off switches and tank vents shall be submitted along with the plans.

- Once the specific plans are received a permit will be issued by our office to grant permission to begin installation of the fuel delivery system.

- Installation shall be in accordance with the North Carolina Fire Code and NFPA 30 standard.

- All hydrostatic and pressure tests for tanks, piping and dispensers shall be witnessed by the Fire Marshal’s Office before any tanks or lines are backfilled.

- Contact the Fire Marshal’s Office to witness the setting of the tanks.

- Exit/Emergency Lighting

  - Exit sign is not indicated on right rear door, only an interior emergency light is shown on plans.

  - Both rear exit discharges do not indicate any exterior emergency lights on the plans.

- Installation acceptance testing.

  - A fire suppression system acceptance test is required for the kitchen hood system.

  - Underground tank and piping testing is required before backfilling.

  - Schedule all inspections with the Fire Marshal’s Office.

  - 910-893-0740

- Notes

- A complete set of construction documents will be required for the underground fuel tank installation.

- Fixed fire suppression system will require additional permit and plans submitted.

- Please contact the Fire marshal’s office to schedule fire suppression testing, underground storage tanks testing, underground piping testing and fire final inspection when work is complete.

- Harnett County Fire Marshal’s Office 910-893-0740

Please review the plans and adhere to any notes and alterations that were made in addition to the original designed plans. These remarks are for the plans that were submitted and its original intent. If you have any questions please do not hesitate to contact me.  We look forward to working with you during the construction period.

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal

rsullivan@harnett.org