Fire Marshal Division

January 23, 2025

Star Life Safety Inc.

1000 N. Main Street, Suite 201

Fuquay-Varina, NC 27526

Re:	Duke Energy – Mobile Substation

1269 Jonesboro Road

Dunn, NC 28334

Application Number – BCOM2408-0012

To Whom It May Concern,

Thank you for submitting the fire alarm plans for Duke Energy Mobile Substation. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Fire Alarm System

- Location and detail of power connection.

- Classification of the supervisory station.

- The shop drawings shall include the seal of a professional engineer or shall be directly designed off of the original design plans of the engineer of record.

- Certificate of Completion for Fire Alarms

- The licensed fire alarm contractor shall perform a 100% pre-test on the installed or modified system prior to scheduling a fire alarm test with the fire code official.  The contractor shall provide the fire code official with a completed copy of the NFPA 72 Record of Completion certificate prior to the start of the witnessed test.  The fire alarm contractor shall produce a monitoring report from UL-listed central station detailing the results of the 100% pre-test

- Approved Plans on Site – All inspections of the fire alarm system will require that a stamped set of plans (with the Harnett County review stamp) be on site for review.  The inspector has the right to disapprove the inspection if the Harnett County approved set of plans are not on location.

- Fire Alarm Device Labels and Zone Maps – All fire alarm detection and notification devices shall be labeled with the identification shown on the fire alarm zone map and fire alarm control panel.  The devices shall be labeled utilizing standard mapping symbols.  A clean plan with devices accurately labeled shall be provided to the fire inspector upon system inspection.

- Duct Detectors - Where a building fire alarm system is provided or required, duct detectors shall be interconnected with the fire alarm system.  Duct detectors shall activate as a supervisory condition on the fire alarm control panel.

- Remote indicators are required regardless of the presence of a building’s fire alarm system.  If the building does not have a fire alarm system, the duct detectors shall be outfitted with an audible/visual device that alerts upon activation.

- Minimum Sound Pressure - The audible alarm notification appliances shall provide a minimum sound pressure level of 90 dBA in mechanical equipment rooms and 60 dBA in other occupancies and throughout every occupiable space within the building.

- Final Inspection – The final inspection of the permitted fire alarm system will encompass the following:  100% testing of all detection devices, testing of all supervisory and trouble signals related to the system, visual inspection of all notification appliances, inspection of all communication signals, and other items that might be required by the inspector.

- Fire Alarm Monitoring Report - Prior to scheduling a fire alarm test, the licensed fire alarm contractor shall perform a 100% pretest and produce a monitoring report from the UL-listed central station that details all the signals received during that pretest.

- Notes

  - A final fire inspection is required. Please contact this office direct to schedule fire inspection at 910-893-0740.

Thank you again for submitting the plans for Duke Energy Mobile Substation. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal

rsullivan@harnett.org

Bottom of Form

Top of Form