Fire Marshal Division

January 21, 2025

Ron W. Webb

1659 W. Hanrahan Road

Ayden, N.C.  28513

RE: 	Mount Pisgah Free Will Baptist Church

145 Prospect Church Road

Erwin, NC 28339

Re: Application Number – BCOM2501-0001

To Whom It May Concern,

Thank you for submitting revised plans for the new church addition. The plans have been reviewed by a qualified code enforcement official for compliance with the North Carolina Fire Prevention code and all other fire protection regulations. The following are items that will need to be addressed before a final inspection of this project can be completed. The items are listed and described below.

- Life Safety Plan

- Could not locate the life safety plan as indicated in Appendix B, only a sheet that stated “occupant content” on page A-5.

- The life safety plan needs to include occupancy load calculations for each room or space, show diagonal distance of building to verify exit placements, indicate maximum travel distances to exits, and show fire extinguisher locations. This information was not included in occupant content page A-5.

- Multi-purpose room shows a perimeter area that states “life safety egress space exempt”.  This area needs to be calculated in the floor space square footage for occupancy load calculation totals.

- Fire Extinguishers

  - Fire extinguishers shall be placed in approved locations and may be field verified on final inspection. The fire extinguishers provided shall have a minimum rating of 2A 10 B: C.

  - Fire extinguisher shall be installed not to exceed 75’ distance of travel.

  - This information needs to be shown on the life safety plan.

Bottom of Form

- Emergency Illumination

  - Emergency illumination is required to meet minimum foot candle illumination for all portions of the means of egress, including the exit discharge, this was not indicated on the exit discharge at all exits.

  - Emergency lights not indicated in electrical room 109 and multi-media room 104.

- Exit Signs

  - Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of the N.C. Fire Code.

  - Exit signs need to be added at multi-purpose room exit doors leading to rear corridor 115 and at exit doors leading to lobby 101 from multi-purpose room.

  - Add directional exit sign at rear corridor 115 indicating exit arrow towards rear lobby exit door.

- Panic and Fire Exit Hardware

  - Doors serving rooms and spaces with an occupant load of 50 or more in a “Group A” occupancy shall not be provided with a latch or lock other than panic hardware or fire exit hardware, this was not indicated on the plans.

- Commercial Hood and Duct Systems

  - A type 1 hood shall be installed at or above all commercial cooking appliances and domestic cooking appliances used for commercial purposes that produce grease or smoke.

  - Each required commercial kitchen exhaust hood and duct system required to have a type 1 hood shall be protected with an approved automatic fire-extinguishing system installed in accordance with the fire code.

- Acceptance Test of Commercial Hood System

- Submit kitchen hood fire suppression system plans and specifications for approval prior to installation.

- An acceptance test will be conducted by the Fire Marshal’s office once system has been installed and pre-tested.

- Installation shall be per architectural and system submittals and compliant with NFPA-17A.

- Knox Box

- A Knox box is required to be installed on the building.

- An application /order form has been attached to the review comments.

  - https://www.knoxbox.com/commercial-knox-boxes/

- Duct Smoke detectors.

  - Smoke detectors installed in ducts shall be listed for the air velocity, temperature and humidity present in the duct. Duct smoke detectors shall be connected to the building’s fire alarm control unit when a fire alarm system is required by Section 907.2.  Activation of a duct smoke detector shall initiate a visible and audible supervisory signal at a constantly attended location and shall perform the intended fire safety function in accordance with this code and the International Mechanical Code. Duct smoke detectors shall not be used as a substitute for required open area detection.

- Fire Alarm System

  - Appendix B indicated there was no fire alarm system, generic plans were submitted with the revised plans, this needs to be corrected on Appendix B Summary Sheet.

  - Battery calculations were not submitted with fire alarm plans.

  - The location of the fire alarm control panel is not shown on the plans.

  - Manual pull stations were not indicated at multi-purpose room exit doors leading to rear corridor 115 and exit doors leading to lobby 101.

  - Horn/strobes need to be added to rooms 104, 109 and 110.

- Fire Alarm System Shop Drawings

- Fire alarm plans, shop drawings and specifications from the licensed installing contractor shall be submitted prior to work beginning, there was no fire alarm plans submitted at this time.

- A rough in inspection is required.

- A final acceptance test is required. (100%)

- Notes

- Please contact the Fire marshal’s office to schedule fire final inspection when work is complete, 910-893-0740.

Thank you again for your submission of revised plans for the new church addition. These remarks are for the plans that were submitted and its original intent. If you have any questions, please do not hesitate to contact me. We look forward to working with you during the construction period.

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal

rsullivan@harnett.org