[image: image1.jpg]




Fire Marshal Division
February 5, 2026
Johnson Controls
Attn: Zac Johnson

540 Civic Blvd.
Raleigh, NC  27610
Re:
Cape Fear Valley Pediatric Psychiatric Facility

186 Crested Iris Drive

Lillington, NC 27546
Application Number: BCOM2501-0010
To Whom It May Concern,

Thank you for submitting the plans for the fire alarm system. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the facility can be given.  These items are outlined and described below.
· Fire Doors 
· Fire doors with hold open devices must have smoke detectors located no more than 5 feet of the corridor doors.  Two sets of corridor doors are spaced incorrectly - at doors between room 111 & room 120A, and at doors between room 126 & room 134.
· Smoke Detectors

· Corridor spacing between smoke detectors shall be no more than 30 feet spaced apart.  Smoke detectors are not spaced correctly in corridors between smoke detectors M1-17 & M1-18, and at smoke detectors M1-19 & M1-20.
· Manual Pull Stations

· Manual pull station is missing at required secondary exit between room 124 & room 122.  
· Exit leading into outdoor recreation area and at rear of outdoor recreation area does not have manual pull stations indicated either, if these are not required exits, then the pull stations can be omitted.  
· Applicable Codes & Standards

· The wrong version of NFPA 72 is indicated on page FA-001 under Applicable Codes & Standards.  This should be indicated as NFPA 72, 2013 version instead of the 2016 version.
· Fire Alarm System Notes:
All items in notes are to be completed at the time of final.

· Provide a record of completion.
· Label all devices before acceptance testing, date stamp standby batteries in FACP and extender panels

· The Fire marshal’s office will complete an acceptance test at completion of project. 
· Provide a copy of account history after the acceptance test is completed and approved.
· Provide an accurate zone map at the FACP and remote annunciator panel.
· All work/installation shall be compliant with the NCSFC and NFPA 72.
· Call Fire Marshal’s office to schedule the fire alarm acceptance test. (910-893-7525 Opt. 1))
Thank you again for submitting the plans for the fire alarm system.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan 
Deputy Fire Marshal
rsullivan@harnett.org

