**May 5, 2025**

**RE: Katelyn Armstrong**

**203 E Jackson Boulevard**

**Erwin, NC 28339**

**Permit # - BCOM2504-0004**

To Whom It May Concern,

Thank you for submitting the change of use plans for the law office. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents. There are some items that were found during the plan review process that need to be addressed before a final inspection of the updated facility can be given. These items are outlined and described below.

* **Fire Extinguishers**
* The fire extinguishers provided shall have a minimum rating of 2A:10BC and shall not be installed higher than five feet above the finished floor.
* **Emergency Lighting**
* All emergency lighting shall be in proper operating condition at the time of final inspection.
* The means of egress, including the exit discharge, shall be illuminated at all times.
* **Physical Address**
* Address numbers attached to the building shall be at least six inches in height and shall be contrasting in color to the background it is attached to.
* **Notes**
* A final inspection is required for this property.
* Please call 910-893-0742 to schedule a date and time to conduct a final inspection.

Thank you again for submitting the plans for the salon. Please review the plans and

adhere to any notes and alterations that were made in addition to the original drawings.

These remarks are for the plans that were submitted and its original intent. These remarks

do not apply if the original intent changes or what was submitted on the above date

changes. If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction

period!

Sincerely,



Matthew Starling

Deputy Fire Marshal

mstarling@harnett.org