Fire Marshal Division

April 8, 2025

Joanie Belcher

1950 Craig Road, Suite 300

St. Louis, MO 63146

Re:	Scooters Coffee

130 Brandywine Court

Cameron, NC 28326

Application Number BCOM2504-0006

To Whom It May Concern,

Thank you for submitting the plans for the Scooter’s Coffee. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Fire Extinguishers

  - Fire extinguishers shall be placed not to exceed 75’ travel distance.

  - The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than 5 feet above the finished grade.

- Physical Address

- The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

- The numbers used to make up the physical address shall be at least 6 inches in height.

- Emergency Illumination

- Emergency illumination is required to meet minimum foot candle illumination for all portions of the means of egress, including the exit discharge.

- Exit Signs

- Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of the N.C. Fire Code.

- Knox Box

- A Knox box is required to be installed on the building.

- An application /order form has been attached to the review comments.

  - https://www.knoxbox.com/commercial-knox-boxes/

- Bottom of Form

- Notes

  - Please schedule fire final inspection through the fire marshal’s office 910-893-0740

Thank you again for submitting the plans for the Scooter’s Coffee. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal