Fire Marshal Division

August 1, 2025

Wilson Office

213 E. Nash St.

Wilson, NC 27893

Re: Dollar General (Erwin)

NC 55 E

Erwin, NC 28339

Application Number BCOM2504-0008

To Whom It May Concern,

Thank you for submitting the plans for the new Dollar General. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

Plan Review Notes

- A Knox Box is required to be installed on the building.

- The physical address numbers shall be mounted on the building. They should be a minimum 6” in height and visible from the roadway.

- The fire extinguishers are required to be properly mounted and tagged by a fire extinguisher company.

- Ensure that the emergency lighting is adequate for the sales area.

- The rear storage area shall not have any combustible storage greater than 12 feet in height.

- The fire apparatus access road shall extend to within 150 feet of all portions of the building.

- BDA survey will need to be conducted due to being over 7500sqft.

- A fire final inspection is required. Call 910-893-7525 Opt. 1 to schedule.

Thank you again for submitting the plans for the new Dollar General. Please review the plan review notes and if you have any questions, please do not hesitate to call this office.

Sincerely,

Leslie Jackson

Chief Deputy Fire Marshal