Fire Marshal Division

May 8, 2025

Triangle Home Pros

6312 Lauraca Lane

Fuquay-Varina, NC 27526

Re:	Highway 42 Mini Storage, Bldg. C

94 Lunker Ln.

Holly Springs, NC 27540

Application Number BCOM2505-0002

To Whom It May Concern,

Thank you for submitting the plans for the mini storage building. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

Fire Extinguishers

  - Fire extinguishers shall be placed not to exceed 75’ travel distance.

  - The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than 5 feet above the finished grade.

Bottom of Form

Fire Department Access

  - The fire department access shall extend to within 150 feet of all portions of the facility, building C does not meet this requirement.

  - The fire department access road shall be of an unobstructed width of not less than 20 feet and shall have an unobstructed vertical clearance of not less the 13 feet 6 inches.

Knox Box

- The main entry gate must have a Knox entry key system installed for fire department access, contact our office for further details if needed.

- Emergency Illumination

  - Emergency illumination is required to meet minimum foot candle illumination for all portions of the means of egress, including the exit discharge.

- Exit Signs

  - Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of chapter 10.

- Building Code Summary

  - Appendix B building code summary is not completely filled out, missing designer contacts & life safety information.

- Notes

- Please schedule a final fire inspection through the Fire Marshal’s Office at

910-893-0740

Thank you again for submitting the plans for the mini storage building.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal

rsullivan@harnett.org