[image: image1.wmf]

0



Fire Marshal Division
April 21, 2026
Anisa Poole
657 West Road
Cameron, N.C.  28326
Re:
Dream Builders Leadership Academy

2277 NC 24

Cameron, N.C. 28326
Application Number BCOM2507-0011
To Whom It May Concern,
Thank you for submitting the plans for the Academy. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

· Fire Extinguishers
· Fire Extinguishers shall be 2A:20BC and shall be placed with a travel distance to not exceed 75’

· Fire extinguishers are to be mounted no higher than 5’ above the finished floor.

· 404.2 Fire Safety and Evacuation Plans 

· An approved fire safety and evacuation plan shall be prepared, posted and maintained for Group E occupancies.

· 1006.1 Illumination Required
· The exit discharge shall be illuminated at all times the building spaces served by the means of egress is occupied 
· Illumination level in all areas of the means of egress shall not be less than 1 foot-candle at the walking surface and shall have emergency power supply. 
· Notes

· A final fire inspection is required. 
· Please contact Harnett Central Permitting Office at 910-893-7525, option 1 to schedule the final inspection.
Thank you again for submitting the plans for the Academy. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,
Roger Sullivan
Roger Sullivan
Deputy Fire Marshal
Bottom of Form

Top of Form

[image: image2.jpg]



_1525259659.unknown

