**August 27, 2025**

**RE: Harnett County Jetport Hanger Bathroom Addition**

**497 Airport Road**

**Lillington, NC 27546**

To Whom It May Concern,

Thank you for submitting the plans for the bathroom addition. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents. There are some items that were found during the plan review process that need to be addressed before a final inspection of the updated facility can be given. These items are outlined and described below.

* **Fire Extinguishers**
* The fire extinguishers provided shall have a minimum rating of 2A:10BC and shall not be installed higher than five feet above the finished floor.
* These were not found on the plans, so ensure they all meet the 75’ travel distance.
* **Emergency Lighting**
* All emergency lighting shall be in proper operating condition at the time of final inspection.
* The means of egress, including the exit discharge, shall be illuminated at all times.
* The means of egress illumination shall not be less than 1 foot-candle at the walking surface.
* **Notes:**
* A final fire inspection is required at the conclusion of construction.
* Schedule fire inspections through the Fire Marshal’s Office at 910-893-0742.

Thank you again for submitting the plans for the bathroom addition. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.

These remarks are for the plans that were submitted and its original intent. These remarks

do not apply if the original intent changes or what was submitted on the above date

changes. If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction

period!

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal

rsullivan@harnett.org