Fire Marshal Division

September 11, 2025

Moonlite Electric & Construction

104-C Woodwinds Industrial Court

Cary, NC 27511

Re: 	Temporary Construction Trailers

3544 US 401 S

Lillington, NC 27546

Application Number BCOM2509-0004

To Whom It May Concern,

Thank you for submitting the construction trailer plans. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Fire Extinguishers

  - Fire extinguishers shall be placed in approved locations and may be field verified on final inspection. The fire extinguishers provided shall have a minimum rating of 2A 10 B: C.

  - Fire extinguisher shall be installed not to exceed 75’ distance of travel.

Bottom of Form

- Emergency Illumination

  - Emergency illumination is required to meet minimum foot candle illumination for all portions of the means of egress, including the exit discharge.

- Exit Signs

  - Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of chapter 10.

Thank you again for submitting the plans for the construction trailer. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal

rsullivan@harnett.org