[image: image1.jpg]




Fire Marshal Division

March 11, 2026
Fredy Castro Guerro
147-E Main Street

Coats, N.C.  27521
Re:
Coats Tire & Auto Open Shelter

34 N. McKinley Street

Coats, NC 27521
Application Number BCOM2605-0005
To Whom It May Concern,
Thank you for submitting the plans for the open shelter. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.
· Fire Extinguishers 
· Fire extinguishers shall be placed not to exceed 75’ travel distance.

· The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than 5 feet above the finished grade.
· Bottom of Form

· Notes
· Please schedule a final fire inspection through the Harnett County Central Permitting Office at (910) 893-7525, option 1.
Thank you again for submitting the plans for the open shelter.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. 
These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org
