[image: image1.jpg]




Fire Marshal Division

March 24, 2026
Lonal Whittenton
409 Chic Ennis Road

Coats, NC  27521
Re:
Twice Told Treasures Antique Mall

3695 US 301 N

Dunn, NC 28334
Application Number BCOM2603-0003
To Whom It May Concern,
Thank you for submitting the plans for the Antique Mall. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.
· Fire Extinguishers
·  The fire extinguishers provided shall have a minimum rating of 2A10BC and shall not be mounted higher than 5 feet above the finished floor level.
·  All fire extinguishers shall be properly mounted and tagged by a fire extinguisher company. 
· Travel distance to a fire extinguisher shall not exceed 75 feet.
· Address Numbers
· The physical address shall be installed on the building so that it is visible from the street. Minimum 6” in height and a contrasting color.
· Panic Hardware
· UL 305 listed panic hardware is required on exit doors serving a room/space with an occupant load >50. 
· All exit doors will be required to have panic hardware and must swing in the direction of travel.
· Means of Egress Illumination

· The means of egress illumination shall not be less than 1 foot-candle at the walking surface.
· The means of egress, including the exit discharge shall be illuminated all times when the building is occupied.
· Exit/Emergency light exit signs need to be installed at all exit doors.
· Notes
· A final fire inspection is required.

· Schedule all fire inspections through Harnett County Central Permitting at (910) 893-7525, option 1.  
Thank you again for submitting the plans for the Antique Mall. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office. 

Sincerely,
Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org

