[image: image1.jpg]




Fire Marshal Division
April 15, 2026
Megan Toler
Centerpoint Integrated Solutions

1626 Cole Blvd. Suite 125

Lakewood, CO 80401

RE: 
The UPS Store 

183 Mittie haddock Dr.


Cameron, NC 28326
Application Number: BCOM2604-0004
To Whom It May Concern,
Thank you for submitting the plans for the building upfit.  The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.
· Fire Extinguishers
· The fire extinguishers provided shall have a minimum rating of 2A:10BC and shall not be installed higher than five feet above the finished floor.
· Travel distance shall not exceed 75 feet.
· Bottom of Form

· Emergency Lighting
· All emergency lighting shall be in proper operating condition at the time of final inspection.

· Illumination requirements also include the exit discharge.
· Exit Signs
· Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of chapter 10 of the NC Fire Code.
·  Physical Address

· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.
· The numbers used to make up the physical address shall be at least six inches in height. 
· Notes
· A final fire inspection is required. Please schedule all inspections through the Harnett County Permitting Office at 910-893-7525, option 1.
Thank you again for submitting the plans for the building upfit.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,
Leslie Jackson

Leslie Jackson
Chief Deputy Fire Marshal

lrjackson@harnett.org
