[image: image1.jpg]




Fire Marshal Division
June 2, 2026
RE: 
Office Space

1198 Mabry Road

Angier, NC 27501
Application Number BCOM2604-0015
To Whom It May Concern,
Thank you for submitting the plans for the Office Space.  The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

·  Fire Extinguishers
· Fire extinguishers shall be placed in approved locations, one in the area of the rear exit area and one in the front entrance area, maximum travel distance to a fire extinguisher not to exceed 75 feet.
· The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than 5 feet above the finished floor.
Bottom of Form

·  Emergency Lighting/Exit Signs
· All emergency lighting/exit signs, provided prior to up fit, shall be in proper operating condition at time of final inspection.

· Any changes made in illumination requirements, due to equipment placement or storage arrangements, shall be addressed before final inspection.
· The means of egress, including the exit discharge shall be illuminated all times when the building is occupied.
·  Knox Box

· Keys for front entrance door shall be provided to be placed in the existing Knox box installed on the premises or one must be installed if not already present.
· Physical Address (i.e.: suite Number if Applicable)
· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.
· The numbers used to make up the physical address shall be at least 6 inches in height with a minimum stroke width of ¾ inch.
· The physical address needs to be posted on the rear of the building also. 
· Panic Hardware
· UL 305 listed panic hardware is required on exit doors serving a room/space with an occupant load >50.  
· Final Inspection call Harnett County Central Permitting 910-893-7525 Opt. 1 to schedule.
Thank you again for submitting the plans for the Office Space.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org
