[image: image1.jpg]




Fire Marshal Division
May 14, 2026
IJJ Atlantic LLC
Attn: William Moore
(405) 425-9809
william@ijjatlantic.com
RE: 
IJJ Atlantic Jiu Jitsu Training Facility

279 NC 24

Cameron,  NC 28326
Application Number: BCOM2605-0005
To Whom It May Concern,
Thank you for submitting the plans for the new business.  The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.
· Fire Extinguishers
· The fire extinguishers provided shall have a minimum rating of 2A:10BC and shall not be installed higher than five feet above the finished floor.
· Travel distance shall not exceed 75 feet.
· Extinguishers were not marked on the plans.
· Bottom of Form

· Emergency Lighting
· All emergency lighting shall be in proper operating condition at the time of final inspection.

· Illumination requirements also include the exit discharge.
· Exit Signs
· Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of chapter 10 of the NC Fire Code.

· Knox Box
· A Knox box will be required to be installed to the front of the building with access keys inside. Keys will need to be on site for the final inspection. If there is already a Knox box installed, no need for another. Just have keys ready for final inspection.
·  Physical Address

· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.
· The numbers used to make up the physical address shall be at least six inches in height. 
· Address and suite numbers also need to be on rear access doors.
· Foam Plastic Materials

· Foam plastic materials being used as wall coverings can not be used unless it meets the testing criteria as listed in section 2603.9 of the NC Building Code (NFPA 286 – with the acceptance criteria of section 803.1.2.1, FM 4480, UL 1040 or UL 1715).
· Occupant Capacity

· The occupant capacity will be limited to 49 occupants due to the doors swinging inward.  

· Notes
· A final fire inspection is required. Please schedule all inspections through the Harnett County Permitting Office at 910-893-7525, option 1.
Thank you again for submitting the plans for the new business.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org
910-893-0742
