[image: image1.jpg]




Fire Marshal Division
June 10, 2026
Southeastern Construction of Buies Creek
P.O. Box 4200 
Buies Creek, NC 27506
Re:
Rumley Center Renovation

140 Day Dorm Road

Lillington, NC 27546
Application Number – BCOM2606-0001
To Whom It May Concern,
Thank you for submitting the plans for the Rumley Center renovation. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below. 
· Fire Extinguishers
· Fire Extinguishers shall be 2A:20BC and shall be placed with a travel distance not to exceed 75’

· Fire extinguishers are to be mounted no higher than 5’ above the finished floor.

· Means of Egress Illumination Required
· The means of egress, including the exit discharge shall be illuminated at all times when the building spaces served by the means of egress is occupied. 

· Illumination level in all areas of the means of egress shall not be less than 1 foot-candle at the walking surface and shall have emergency power supply.

· Fire Alarm System Shop Drawings
· Fire alarm plans, shop drawings and specifications from the licensed installing contractor shall be submitted prior to work beginning.

· A rough-in inspection is required.

· A final acceptance test is required. (100%) 

· Notes

· A final fire inspection is required.  Please contact the Harnett County Central Permitting Office to schedule at (910) 893-7525, option 1.
Thank you again for submitting the plans for the Rumley Center renovation. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org
