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Fire Marshal Division
July 14, 2026
RE: 
Achievement Charter Academy Modular Building

25 Buttonwood Ct.


Fuquay-Varina, NC 27526
Re: Application Number – BCOM2606-0009
To Whom It May Concern,
Thank you for submitting plans for the Modular Building. The plans have been reviewed by a qualified code enforcement official for compliance with the North Carolina Fire Prevention code and all other fire protection regulations. The following are items that will need to be addressed before a final inspection of this project can be completed. The items are listed and described below.
· Physical Address

·  The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

· The numbers used to make up the physical address shall be at least 6 inches in height.   
· Fire Extinguishers 
· Fire extinguishers shall be placed in approved locations and may be field verified on final inspection. The fire extinguishers provided shall have a minimum rating of 2A 10 B: C. 
· Fire extinguisher shall be installed not to exceed 75’ distance of travel.
Bottom of Form

· Emergency Illumination
· Emergency illumination is required to meet minimum foot candle illumination for all portions of the means of egress, including the exit discharge.  Emergency illumination for exit discharge was not noted on electrical plans.
· Exit Signs
· Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of the N.C. Fire Code. 

· Knox Box
· A Knox box is required to be installed on the building.
· An application /order form has been attached to the review comments.
· https://www.knoxbox.com/commercial-knox-boxes/
· Fire Alarm System Shop Drawings
· Fire alarm plans, shop drawings and specifications from the licensed installing contractor shall be submitted prior to work beginning, there was no information on the fire alarm panel, devices & appliances specification sheets or battery calculations.

· A rough in inspection is required.

· A final acceptance test is required. (100%) 

· Notes
· Please contact Harnett County Central Permitting Office at 910-893-7525 Opt. 1. For scheduling.
Thank you again for your submission of plans for the Modular Building. These remarks are for the plans that were submitted and its original intent. If you have any questions, please do not hesitate to contact me. We look forward to working with you during the construction period.

Sincerely,

Leslie Jackson
Leslie Jackson
Chief Deputy Fire Marshal

