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Fire Marshal Division

August 6, 2026
Imperial Self Storage Development Inc.
110 Wild Winds Drive
Coats, NC  27521
Re:
Lakeside Storage Building G

4271 Neills Creek Road

Angier, NC 27501
Application Number BCOM2607-0011
To Whom It May Concern,
Thank you for submitting the plans for the storage building. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.
· Fire Extinguishers 
· Fire extinguishers shall be placed not to exceed 75’ travel distance.

· The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than 5 feet above the finished grade.
· Bottom of Form

· Fire Department Access

· The fire department access shall extend to within 150 feet of all portions of the exterior of the building.

· The fire department access road shall be of an unobstructed width of not less than 20 feet and shall have an unobstructed vertical clearance of not less the 13 feet 6 inches, an all weather surface and capable of supporting 75,000 pounds.
· Fire Protection Water Supply

· There must be a fire hydrant within 400 feet of the building as measured by an approved road route to the farthest point of the building.  Any future buildings will have to meet this requirement by installing on site fire hydrants.  

· Physical Address
· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

· The numbers used to make up the physical address shall be at least six inches in height.
· Knox Box

· A Knox box will be required to be installed in a centrally located area and be equipped with keys to access all buildings. Keys will need to be on site for the final inspection.
· If there are any fences or gates, a Knox box will be required for gate or fence entry.
Notes
· A final fire inspection is required.  Please schedule all fire inspections through the Harnett Central Permitting Office at (910) 893-7525, option 1.
Thank you again for submitting the plans for the storage building.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org
