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Fire Marshal Division
October 8, 2026
Frank Taylor
PO Box 390 

Coats, NC 27521

Re:
Church of God of Prophecy

7819 NC 27 E


Coats, NC 27521

Application Number – BCOM2610-0002
To whom it may concern,
Thank you for submitting the plans for the storage addition. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

· Fire Extinguishers
· Fire Extinguishers shall be 2A:20BC and shall be placed with a travel distance to not exceed 75’

· Fire extinguishers are to be mounted no higher than 5’ above the finished floor.
· Means of Egress Illumination Required
· If the addition is closed in the means of egress, including the exit discharge shall be illuminated at all times when the building spaces served by the means of egress is occupied. 

· Illumination level in all areas of the means of egress shall not be less than 1 foot-candle at the walking surface and shall have emergency power supply.

· Notes

· A final fire inspection is required. Please contact Harnett County Central Permitting office direct to schedule fire inspection at 910-893-7525 Opt. 1.

Thank you again for submitting the plans for the storage addition. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Leslie Jackson
Leslie Jackson
Chief Deputy Fire Marshal

lrjackson@harnett.org
