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Fire Marshal Division

October 22, 2026
Mills Construction Co. of SC, Inc.
Attn: Corey Maner
P.O. Box 6171
Raleigh, N.C.  27628
Re:
Maynard Crossing Apartments Building 100 (1221-3)

100 Maynard Lake Road

Erwin, N.C. 28339
Application Number BCOM2610-0007
To Whom It May Concern,
Thank you for submitting plans for Maynard Crossing Apartments Building 100. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

· Automatic fire-extinguishing systems.
· A construction permit is required for the fire sprinkler system installation before any such work commences.  Submit complete construction documents that include the hydraulic calculations for the system. The system shall also be designed consistent with the architectural design documents and specifications.  Construction documents shall include detail as described in NFPA 13 standard for automatic sprinkler system installation. Contractor must obtain construction permit for the fire sprinkler system before commencement of any work.

· Fire alarm construction permits.

· A construction permit is required for the fire alarm installation.  Submit complete shop drawings consistent with the architectural design documents and specifications.  Shop drawings shall include detail as described in Section 907.1.2 of the NC State Fire Code.  
· Contractor must obtain the construction permit for the fire alarm system before commencement of any work.
· Emergency Responder Radio Coverage (BDA System) if applicable, only for all buildings over 12,000 square feet.
· A construction permit is required for installation of emergency responder radio coverage system.  Submit complete shop drawings consistent with the architectural design documents and specifications. Provide specifications, cut sheets and information on all appliances, devices and wiring to be installed for the BDA system.  
· A preliminary evaluation plan (raw survey) of the current outside radio signal strength shall be developed and submitted.  
· Private fire hydrants.

· A construction permit is required for the installation or modification of private fire hydrants.  Contractor must obtain the construction permit for the private hydrants before commencement of any work.
· Physical Address

· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

· The numbers used to make up the physical address shall be at least 6 inches in height.   

· Knox Box


· A Knox Box secure key box shall be installed on the new building that houses all keys to all the doors within the building in which the fire department would need access to in the event of an emergency. https://www.knoxbox.com/commercial-knox-boxes
· The box shall be mounted 60 inches in height.  Coordinate exact location with the Fire Marshal’s Office staff.
· Fire Flow (NFF)
· Provide a fire flow analysis for the building(s) and determined by an approved method.  NC Fire Code Appendix B is acceptable method.  

· Private fire service water mains shall be installed according to NFPA 24.  All fire protection water mains shall be inspected by a fire official before covering.  A contractor’s underground flush and test certificate is required at time of fire official inspection.  

· Control room identification.
· All rooms containing controls for air conditioning equipment, sprinkler risers and valves, or other fire detection, suppression, or control elements shall by physically identified in terms of use (i.e., FACP Room, Electrical Room, Riser Room).
· State of Compliance.

· Before requesting final approval of the installation, where required by the fire code official, the installing contactor shall furnish a written statement to the fire code official that the subject fire protection system has been installed in accordance with the manufacture’s specifications and the appropriate installation standard.  Any deviations from the design standards shall be noted and copies of the approvals for such deviations shall be attached to the written statement.  
· Fire Extinguishers
· The fire extinguishers provided shall have a minimum rating of 2A 10B:C and shall not be installed higher than 5 feet above the finished floor.

· Fire extinguishers shall be serviced and tagged on a yearly basis by an authorized company.
· Fire extinguisher shall be installed not to exceed 75’ distance of travel.
· Acceptance tests. 

· A complete acceptance test is required to be witnessed by a representative from the fire marshal’s office in conjunction with the installing contractor for each of the following.  

· Visual Inspection of Underground Line (with proper restraints)

· Hydrostatic Test and Flush of Underground Line

· Above Ceiling Inspection of ALL pipe and fittings

· Hydrostatic Test of ALL piping

· Flow Test of sprinkler/standpipe system

· 100 % test of Fire Alarm System

· Record of completion. 

· A record of completion in accordance with NFPA 72 verifying that the system has been installed in accordance with the approved plans and specifications shall be provided.
Thank you again for submitting plans for Maynard Crossing Apartments Building 100.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office. 

Please schedule all fire inspections through the Harnett County Central Permitting Office at (910) 893-7525, option 1.
Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

