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Fire Marshal Division

October 28, 2026
Mills Construction Co. of SC, Inc.
Attn: Corey Maner
P.O. Box 6171
Raleigh, N.C.  27628
Re:
Maynard Crossing Apartments Picnic Shelter

100 Maynard Lake Road

Erwin, N.C. 28339
Application Number BCOM2610-0010
To Whom It May Concern,
Thank you for submitting plans for Maynard Crossing Picnic Shelter. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

· Fire Extinguishers
· The fire extinguishers provided shall have a minimum rating of 2A 10B:C and shall not be installed higher than 5 feet above the finished floor.

· Fire extinguishers shall be serviced and tagged on a yearly basis by an authorized company.
· Fire extinguisher shall be installed not to exceed 75’ distance of travel.
Thank you again for submitting plans for Maynard Crossing Apartments Picnic Shelter.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office. 

Please schedule all fire inspections through the Harnett County Central Permitting Office at (910) 893-7525, option 1.
Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

