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Fire Marshal Division

October 26, 2026
Mills Construction Co. of SC, Inc.
Attn:  Corey Maner

P.O. Box 6171

Raleigh, NC  27628
Re:
Maynard Crossing Apts. Community Center

90 Maynard Lake Road

Erwin, NC 28339
Application Number FMFW2610-0011
To Whom It May Concern,
Thank you for submitting the plans for the Maynard Crossings Community Center. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.
· Fire Extinguishers
·  The fire extinguishers provided shall have a minimum rating of 2A10BC and shall not be mounted higher than 5 feet above the finished floor level.
·  All fire extinguishers shall be properly mounted and tagged by a fire extinguisher company. 

· Address Numbers
· The physical address shall be installed on the building so that it is visible from the street. Minimum 6” in height and a contrasting color.
· Knox Box
· A Knox Box installation is required for this building

· An order form can be obtained from this office or the box can be order online at www.knoxbox.com.

· Panic Hardware
· UL 305 listed panic hardware is required on exit doors serving a room/space with an occupant load >50. 
· Occupant Load Posting
· The occupant load posting shall be provided by the Fire Marshal’s Office at fire final inspection.

· Means of Egress Illumination

· The means of egress illumination shall not be less than 1 foot-candle at the walking surface.
· The means of egress, including the exit discharge all times when the building spaces served by the means of egress is shall be illuminated at occupied.  
· Notes
· A final fire inspection is required.

· Schedule all fire inspections through the Harnett County Central Permitting Office at (910) 893-7525, option 1.
Thank you again for submitting the plans for the Maynard Crossings Community Center. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office. 

Sincerely,
Roger Sullivan
Roger Sullivan
Deputy Fire Marshal

rsullivan@harnett.org

