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November 4, 2026

RE: 	Razani Flame
	79 E. Main Street
	Coats, NC 27521
	
Application Number: BCOM2610-0012

To Whom It May Concern,

Thank you for submitting the plans for the restaurant.  The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

· Fire Extinguishers
· The fire extinguishers provided shall have a minimum rating of 2A:10BC and shall not be installed higher than five feet above the finished floor.
· Travel distance shall not exceed 75 feet.
· Fire extinguishers must be serviced annually by a qualified fire protection company.
· In addition to the above extinguishers, a portable fire extinguisher shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher

· Bottom of Form
· Emergency Lighting
· All emergency lighting shall be in proper operating condition at the time of final inspection.
· Illumination requirements also include the exit discharge.

· Exit Signs
· Exit signs shall be installed at all required exits. Exit signs shall meet all provisions of chapter 10 of the NC Fire Code.

·  Physical Address
· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.
· The numbers used to make up the physical address shall be at least six inches in height. 
· Address and suite numbers also need to be on rear access doors.


· Knox Box
· A Knox box will be required to be installed to the front of the building with access keys inside. Keys will need to be on site for the final inspection. If there is already a Knox box, just provide keys

· Panic Hardware
· UL 305 listed panic hardware is required on exit doors serving a room/space with an occupant load greater than 50.

· Commercial Kitchen Hoods
· Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned every 6 months by a qualified hood cleaning company.
· Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced every 6 months by a qualified fire protection company.

· Notes
· A final fire inspection is required. Please schedule all inspections through the Harnett County Permitting Office at 910-893-7525, option 1.

Thank you again for submitting the plans for the restaurant.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan

Roger Sullivan
Deputy Fire Marshal
rsullivan@harnett.org
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