Fire Marshal Division

July 23, 2021

Josh Price

T.A Loving Company

Re: Angier & Black River Fire Dept. Addition

309 N. Broad St.

Angier, NC 27501

Application Number FMFW2107-0008

Mr. Price,

Thank you for submitting the plans for the Fire Department addition. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

Plan Review Notes

Sprinklers

# 901.2.1 State of Compliance.

# Before requesting final approval of the installation, where required by the fire code official, the installing contactor shall furnish a written statement to the fire code official that the subject fire protection system has been installed in accordance with the manufacture’s specifications and the appropriate installation standard.  Any deviations from the design standards shall be noted and copies of the approvals for such deviations shall be attached to the written statement.

# 903.4 Sprinkler system monitoring and alarms.

  - All valves controlling the water supply for automatic sprinkler systems and water-flow switches on all sprinkler systems shall be electrically supervised according to the NC State Fire Code.

# 901.5 Installation acceptance testing.

  - Fire-extinguishing systems, all fire protection systems and appurtenances thereto shall be subject to acceptance tests as contained in the installation standards and as approved by the code official.

  - All piping and attached appurtenances subjected to system working pressure shall be hydrostatically tested at 200 psi or 50 psi in excess of the system working pressure, whichever is greater, and shall maintain that pressure without loss for 2 hours. This test is required to be witnessed by a representative from the Harnett County Fire Marshal’s Office.

  - A contractor’s material and test certificate shall be furnished by the trained representative of Fire & Life Safety America, Inc. before final approval.

- 906.1  Fire Extinguishers

- All new and existing fire extinguishers are to be properly mounted and tagged by a fire extinguisher company.

- 505.1  Physical Address

- New addressed numbers shall be of contrasting color and visible from the street

- 1008.1.10  Panic Hardware

- Exit doors servicing assembly area with occupancy load greater than 50 need to have panic hardware.

- 1018.1   Corridor Construction

- Corridors serving greater than 30 in assembly and in business occupancy    class, shall be constructed of 1 hour rated material. The doors in rated corridor shall be 1 hour rated.

Notes

Life safety plan indicates fire alarm, if a fire alarm is to be installed, the   following requirements need to be met

- 907.1.1  Fire Alarm System Construction Documents

- Provide conceptual fire alarm design sealed by electrical engineer.

- 907.1.2  Fire Alarm Shop Drawings

- Provide fire alarm shop drawings from the installing fire alarm contractor.

- This submittal shall include all items required by this code section.

- A fire alarm system construction permit shall be required.

- System rough-in/device location inspection shall be required.

System acceptance test is required at completion of project. (100%)

- All fire inspection request should be made through the Fire Marshal’s Office.

- (910) 893-0740

Thank you again for submitting the plans for the new addition. Please review the plan review notes and if you have any questions, please do not hesitate to call this office.

Sincerely,

Leslie Jackson

Chief Deputy Fire Marshal