## Sheet1
Power Source |  |  |  | Max | Used | Percent Used
ES-200X |  |  |  | 3 | 2.842 | 95
| Circuit |  |  | Max | Used | Percent Used
| Panel Modules |  |  | 3 | 0 | 0
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 1 |  | DP-ES-R | Dress Panel for the ES Series Control Panels |  | 0 | 0 | 0 | 0
|  | 1 |  | TR-CE | Trim Ring for Flush Mounting |  | 0 | 0 | 0 | 0
|  | 2 |  | FCPS-24FS8 | 24Volt, 8 amp Remote Power Supply with 4 NAC circuits |  | 0 | 0 | 0 | 0
| Circuit |  |  | Max | Used | Percent Used
| NAC 1 |  |  | 2.5 | 2.144 | 86
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 2 |  | P2WH-LF | Low Frequency (520 Hz) Sounder/Strobe, White |  | 0 | 0.674 | 0 | 0.674
|  |  | 2 | @ 135 Candela | Candela Rating |  | 0 | 0.674 | 0 | 0.674
|  | 10 |  | PC2WL | L-Series, White, Ceiling-Mountable, Clear Lens, 2-Wire, Horn/Strobe |  | 0 | 1.47 | 0 | 1.47
|  |  | 10 | @ 75 Candela | Candela Rating |  | 0 | 1.47 | 0 | 1.47
| Circuit |  |  | Max | Used | Percent Used
| NAC 2 |  |  | 2.5 | 0 | 0
| NAC 3 |  |  | 2.5 | 0 | 0
| NAC 4 |  |  | 2.5 | 0 | 0
| SLC 1 |  |  | 0.4 | 0.4 | 100
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 7 |  | BG-12LX | Addressable Manual Pull Station |  | 0.0021 | 0.0021 | 0.0021 | 0.0021
|  | 2 |  | H365 | Intelligent Addressable Thermal Detector, White |  | 0.0004 | 0.013 | 0.0004 | 0.013
|  | 85 |  | SD365 | Intelligent Addressable Photoelectric Detector, White |  | 0.017 | 0.5525 | 0.017 | 0.5525
|  | 9 |  | D355PL | Intelligent Non-Relay Duct Smoke Detector. Includes SD355R Detector. |  | 0.0027 | 0.0585 | 0.0027 | 0.0585
|  | 4 |  | MMF-300 | Addressable Monitor Module |  | 0.0016 | 0.0204 | 0.0016 | 0.0204
| Circuit |  |  | Max | Used | Percent Used
| Non-Resettable 1 |  |  | 1 | 0 | 0
| Resettable 1 |  |  | 1 | 0 | 0
| ANN-BUS 1 |  |  | 0 | 0 | 0
| ANN-BUS 2 |  |  | 0 | 0 | 0
| External Source |  |  | 0 | 0 | 0
| IDC 1 (4-Wire/Dry Contact) |  |  | 0.04 | 0 | 0
| IDC 2 (4-Wire/Dry Contact) |  |  | 0.04 | 0 | 0
| IDC 3 (4-Wire/Dry Contact) |  |  | 0.04 | 0 | 0
| IDC 4 (4-Wire/Dry Contact) |  |  | 0.04 | 0 | 0
Power Source |  |  |  | Max | Used | Percent Used
FCPS-24FS8 |  |  |  | 8 | 6.265 | 78
| Circuit |  |  | Max | Used | Percent Used
| NAC 5 |  |  | 3 | 0.387 | 13
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 9 |  | SWL | L-Series, White, Wall-Mounted, Clear Lens, Strobe |  | 0 | 0.387 | 0 | 0.387
|  |  | 9 | @ 15 Candela | Candela Rating |  | 0 | 0.387 | 0 | 0.387
| Circuit |  |  | Max | Used | Percent Used
| NAC 6 |  |  | 3 | 1.911 | 64
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 13 |  | PC2WL | L-Series, White, Ceiling-Mountable, Clear Lens, 2-Wire, Horn/Strobe |  | 0 | 1.911 | 0 | 1.911
|  |  | 13 | @ 75 Candela | Candela Rating |  | 0 | 1.911 | 0 | 1.911
| Circuit |  |  | Max | Used | Percent Used
| NAC 7 |  |  | 3 | 1.911 | 64
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 13 |  | PC2WL | L-Series, White, Ceiling-Mountable, Clear Lens, 2-Wire, Horn/Strobe |  | 0 | 1.911 | 0 | 1.911
|  |  | 13 | @ 75 Candela | Candela Rating |  | 0 | 1.911 | 0 | 1.911
| Circuit |  |  | Max | Used | Percent Used
| NAC 8 |  |  | 3 | 1.911 | 64
|  | Quantity |  | Part Number | Description |  | AC Non-Alarm | AC Alarm | Battery Non-Alarm | Battery Alarm
|  | 13 |  | PC2WL | L-Series, White, Ceiling-Mountable, Clear Lens, 2-Wire, Horn/Strobe |  | 0 | 1.911 | 0 | 1.911
|  |  | 13 | @ 75 Candela | Candela Rating |  | 0 | 1.911 | 0 | 1.911
| Circuit |  |  | Max | Used | Percent Used
| Non-Resettable 2 |  |  | 0.5 | 0 | 0
Power Source |  |  |  | Max | Used | Percent Used
FCPS-24FS8 |  |  |  | 8 | 0.145 | 2
| Circuit |  |  | Max | Used | Percent Used
| NAC 9 |  |  | 3 | 0 | 0
| NAC 10 |  |  | 3 | 0 | 0
| NAC 11 |  |  | 3 | 0 | 0
| NAC 12 |  |  | 3 | 0 | 0
| Non-Resettable 3 |  |  | 0.5 | 0 | 0