Fire Marshal Division

March 15, 2023

Williams Fire Sprinkler Company, Inc.

P.O. Box 1048

Williamson, NC 27892

Re:	Harnett County Schools Central Office Renovation, Fire Alarm

601 Main Street

Lillington, NC 27546

Application Number FMFW2206-0002

To Whom It May Concern,

Thank you for submitting the fire alarm plans and BDA system. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Fire Alarm and BDA Systems Plan Review Notes

- Provide a record of completion.

- Provide a signed monitoring agreement.

- Provide a copy of pretest history from the central station.

- The Fire marshal’s office will complete an (100%) acceptance test at completion of project on both systems.

- Provide a copy of account history after the acceptance test is completed and approved.

- Provide an accurate zone map at the FACP and remote annunciator panel.

- All work/installation shall be compliant with the NCSFC and NFPA 72 and FCC 47 CFR Part 90.219.

- Call Fire Marshal’s office to schedule the fire alarm and BDA systems acceptance test. (910-893-0740)

- Thank you again for submitting fire alarm plans and BDA system.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Roger Sullivan

Roger Sullivan

Deputy Fire Marshal