## MS-10UD-7
MS-10UD-7 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
Main Circuit Board | 1 | x | 0.127 | = | 0.127 | 1 | x | 0.265 | = | 0.265 | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
CAC-5X | 0 | x | 0.001 | = |  | 0 | x | 0.001 | = |  | 60 Minutes | 1
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  | 90 Minutes | 1.5
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | = |  | 120 Minutes | 2
2. Annunciators | [10 empty] | 180 Minutes | 3
ANN-80 | 1 | x | 0.015 | = | 0.015 | 1 | x | 0.04 | = | 0.04 | 240 minutes | 4
ANN-80-W | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LEDs | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
3. Resettable Power
Conventional Detectors | 1 | x | 0.00115 | = | 0.00115
IDC's Used Minus 1 | [5 empty] | 0 | x | 0.04 | =
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
4. Other Devices
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
5. Notification Appliances
NAC 1 |  |  | 0 | = |  |  |  | 2.9 | = | 2.9
NAC 2 |  |  | 0 | = |  |  |  | 0.387 | = | 0.387
NAC 3 |  |  | 0 | = |  |  |  | 0.946 | = | 0.946
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
Resettable 1 |  |  | 0 | = |  |  |  | 0 | =
Non-Resettable 1 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.14315 | Total Alarm Load |  |  |  | 4.538
MS-10UD-7 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.14315 |  |  | x | 24 |  | = | 3.4356
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 4.538 |  |  | x | 0.084 |  | = | 0.38119
Total Current Load | [9 empty] | 3.8168
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 4.5802
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-10UD-7 Charger.
The batteries can be housed in the MS-10UD-7 Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS-10UD-7 Control Panel:
The output current is within the panel's limitations.
MS-10UD-7 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
P2RL @ 75 Candela | 5 | x | 0 | = | 0 | 5 | x | 0.139 | = | 0.695
PC2RL @ 75 Candela | 15 | x | 0 | = | 0 | 15 | x | 0.147 | = | 2.205
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 2.9
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
SRL @ 15 Candela | 9 | x | 0 | = | 0 | 9 | x | 0.043 | = | 0.387
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0.387
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
SRL @ 15 Candela | 22 | x | 0 | = | 0 | 22 | x | 0.043 | = | 0.946
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0.946
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Resettable 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Non-Resettable 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on B17: Remember to select the number for LED's for each ANN-I/O that is added (Maximum 40 LEDs per ANN-I/O).
Note on B18: Maximum 40 LEDs for each ANN-I/O.
Note on B23: Includes 2-wire and 4-Wire detectors.
Note on H49: Select Standby Time in Hours from the dropdown list.
Note on H52: Select the Alarm Time in minutes from the dropdown list.
Note on H55: Select the Derating Factor from the dropdown list.