Fire Marshal Division

May 15, 2024

Brian Gesell

2854 Logan St.

Nashville, TN 37211

Re:	Tractor Supply Company

NC Hwy 210

Lillington, NC 27546

Application Number – FMFW2405-0006

To Whom It May Concern,

Thank you for submitting the plans for Tractor Supply. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Physical Address

- The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

- The numbers used to make up the physical address shall be at least 6 inches in height.

- Fire Department Access

  - The fire department access shall extend to within 150 feet of all portions of the facility (current driveway and parking lot may suffice).

  - The fire department access road shall be of an unobstructed width of not less than 20 feet and shall have an unobstructed vertical clearance of not less the 13 feet 6 inches.

- Fire Safety and Evacuation Plans

  - An approved fire safety and evacuation plan shall be prepared, posted and maintained.

- Fire Extinguishers

  - Fire Extinguishers shall be 2A:20BC and shall be placed with a travel distance to not exceed 75’

  - Fire extinguishers are to be mounted no higher than 5’ above the finished floor.

- Means of Egress Illumination Required

  - The means of egress, including the exit discharge shall be illuminated at all times the building spaces served by the means of egress is occupied.

  - Illumination level in all areas of the means of egress shall not be less than 1 foot-candle at the walking surface and shall have emergency power supply.

- Knox Box

  - Keys for front entrance door shall be provided to be placed in the Knox Box installed on the premises.

- Fire Alarm Systems

- The plans shall include the following:

- Floor Plan that indicates the use of all rooms.

- Locations of all alarm-initiating devices.

- Locations of alarm notification appliances, including candela ratings for visible alarm notification appliances.

- Design minimum audibility level for occupant notification.

- Location of fire alarm control panel, transponders, and notification power supplies.

- Location of annunciators.

- Location and detail of power connection.

- Battery Calculations.

- Conductor type and sizes.

- Voltage drop calculations.

- Manufacturers’ data sheets indicating model numbers and listing information for equipment, devices, and materials.

- Details of ceiling height and construction.

- The interface of fire safety control functions.

- Classification of the supervisory station.

- Systems and components of fire alarm systems shall be listed and approved for the purpose to which they are installed.

- The shop drawings shall include the seal of a professional engineer or shall be directly designed off of the original design plans of the engineer of record.

- Certificate of Completion for Fire Alarms

- The licensed fire alarm contractor shall perform a 100% pre-test on the installed or modified system prior to scheduling a fire alarm test with the fire code official.  The contractor shall provide the fire code official with a completed copy of the NFPA 72 Record of Completion certificate prior to the start of the witnessed test.  The fire alarm contractor shall produce a monitoring report from UL-listed central station detailing the results of the 100% pre-test

- Approved Plans on Site – All inspections of the fire alarm system will require that a stamped set of plans (with the Harnett County review stamp) be on site for review.  The inspector has the right to disapprove the inspection if the Harnett County approved set of plans are not on location.

- Fire Alarm Device Labels and Zone Maps – All fire alarm detection and notification devices shall be labeled with the identification shown on the fire alarm zone map and fire alarm control panel.  The devices shall be labeled utilizing standard mapping symbols.  A clean plan with devices accurately labeled shall be provided to the fire inspector upon system inspection.

- Duct Detectors - Where a building fire alarm system is provided or required, duct detectors shall be interconnected with the fire alarm system.  Duct detectors shall activate as a supervisory condition on the fire alarm control panel.

- Remote indicators are required regardless of the presence of a building’s fire alarm system.  If the building does not have a fire alarm system, the duct detectors shall be outfitted with an audible/visual device that alerts upon activation.

- Minimum Sound Pressure - The audible alarm notification appliances shall provide a minimum sound pressure level of 90 dBA in mechanical equipment rooms and 60 dBA in other occupancies and throughout every occupiable space within the building.

- Final Inspection – The final inspection of the permitted fire alarm system will encompass the following:  100% testing of all detection devices, testing of all supervisory and trouble signals related to the system, visual inspection of all notification appliances, inspection of all communication signals, and other items that might be required by the inspector.

- Fire Alarm Monitoring Report - Prior to scheduling a fire alarm test, the licensed fire alarm contractor shall perform a 100% pretest and produce a monitoring report from the UL-listed central station that details all the signals received during that pretest.

- Sprinkler System Inspections

- Before requesting final approval of the installation, where required by the fire code official, the installing contactor shall furnish a written statement to the fire code official that the subject fire protection system has been installed in accordance with the manufacture’s specifications and the appropriate installation standard.  Any deviations from the design standards shall be noted and copies of the approvals for such deviations shall be attached to the written statement.

- All valves controlling the water supply for automatic sprinkler systems and water-flow switches on all sprinkler systems shall be electrically supervised according to the NC State Fire Code.

- All piping and attached appurtenances subjected to system working pressure shall be hydrostatically tested at 200 psi or 50 psi in excess of the system working pressure, whichever is greater, and shall maintain that pressure without loss for 2 hours. This test is required to be witnessed by a representative from the Harnett County Fire Marshal’s Office.

- A contractor’s material and test certificate shall be furnished by the trained representative of Carolina Fire Protection before approval.

- A piping and hanger inspection is required before closure of ceiling system(s).

- A sprinkler final inspection is required at completion of project.

- Notes

  - A final fire inspection is required. Please contact this office direct to schedule fire inspection at 910-893-0740.

Thank you again for submitting the plans for Tractor Supply. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Leslie R. Jackson

Chief Deputy Fire Marshal

lrjackson@harnett.org

Bottom of Form

Top of Form