Fire Marshal Division

September 3, 2024

RE:	Angier Medical Complex (Shell)

75-91 Logan Court

Angier, NC 27526

Application Number FMFW2408-0011

To Whom It May Concern,

Thank you for submitting the plans for the new business center shell building. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Physical Address

- The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

- The numbers used to make up the physical address shall be at least 6 inches in height.

- Fire Extinguishers

  - Fire Extinguishers shall be 2A:10BC and shall be placed with a travel distance to not exceed 75’

  - Fire extinguishers are to be mounted no higher than 5’ above the finished floor.

- Knox Box

  - A Knox box is required to be installed on the building.

  - https://www.knoxbox.com/store/productConfigurator.cfm?sku=3261

- Notes

- The building plans have been reviewed for fire code compliance as a shell.  Any future occupancy deviating or making ANY changes to the floorplan MUST re-submit for approval.

Thank you again for submitting the plans for the new shell building. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent.

These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Leslie Jackson

Chief Deputy Fire Marshal

lrjackson@harnett.org