April 1, 2025

Oakes Grading Inc.

911 NC 96 Hwy E

Youngsville, NC  27596

RE: 	Champs Convenience

8920 US 401 N

Fuquay-Varina, NC 27526

Application Number: FMFW2503-0001

To whom it may concern,

Thank you for submitting the plans for the installation of underground flammable & combustible liquid tanks at the above location.  The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.

After permit is issued and before final approval:

- Smoking and Open Flames

  - Signs shall be posted in storage and dispensing areas. Signs shall comply with Section 2305.6

- Vehicle Impact Protection

  - Where any portions of the fuel storage or dispensing components are subject to vehicular impact, they shall be protected by meeting the provisions of Section 312 of the North Carolina Fire Code.

- Testing of Dispensers

  - After initial pipe testing and setting of dispensers, the dispensers will be examined and tested.

  - The emergency fuel shut off switch will be tested.Bottom of FormTop of Form

  - Installation shall be in accordance with all North Carolina Fire prevention codes and NFPA 30 standards.

- All hydrostatic and pressure tests for tanks and piping shall be witnessed by the Fire Marshal’s Office.

- Contact the Fire Marshal’s Office to witness the setting of tanks.

- A final Fire inspection is required at the end of the project.

- Call (910) 893-0740 to schedule all fire inspections.

Thank you again for submitting the plans for the new UGST. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Sincerely,

Roger Sullivam

Roger Sullivan

Deputy Fire Marshal