Fire Marshal Division

March 12, 2025

Re:	Pyro Shows East Coast

138 Donald Ray Ln.

Lillington, NC 27546

Application Number – FMFW2503-0002

To Whom It May Concern,

Thank you for submitting the plans for the Magazine Storage Conex Box. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Fire Extinguisher

  - The fire extinguishers provided shall have a minimum rating of 2A10BC and shall not be mounted higher than 5 feet above the finished floor level.

  - All fire extinguishers shall be properly mounted and tagged by a fire extinguisher company.

- Means of Egress Illumination

- The means of egress illumination shall not be less than 1 foot-candle at the walking surface.

- Hazard Identification Signs

- Ensure that all required Hazard identification signage is installed as it regards to pool chemical storage.

- Notes

- A final fire inspection is required.

- Schedule all fire inspections through the Fire Marshal’s Office.

(910)893-0740.

Thank you again for submitting the plans for the Magazine Storage Conex Box. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Sincerely,

Leslie Jackson

Leslie Jackson

Chief Deputy Fire Marshal