Town of Angier Building Inspectors Review of Angier Police Station

* Sheet E-200 - Please add the notes below to the Power Riser notes.



The following are suggestions and/or questions

* Evidence Room and Amory – are these rooms reinforced with higher fire rated walls? Our review, the wall of these two rooms appears to be normal wall board. Would these rooms need a higher fire reinforcement?
* Plumbing fixtures call for manual controls, would an automatic fixture be better, especially in the intake bathroom?
* Grounding of the generator using the rebar for the building itself be better than a rod?