Fire Marshal Division

August 25, 2025

RE: 	Blooms Brew Café & Play

123 N Wilson Avenue

Dunn, NC 28334

To Whom It May Concern,

Thank you for submitting the plans for the change of use.  The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

- Fire Extinguishers

  - The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than five feet above the finished floor.

  - Travel distance shall not exceed 75 feet.

  - In addition to the above extinguishers, a portable fire extinguisher shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher. This is only required if cooking is going to be done.

Bottom of Form

- Emergency Lighting

  - All emergency lighting shall be in proper operating condition at time of final inspection.

  - Illumination requirements also include the exit discharge.

- Knox Box

- A knox box will be required to be installed to the front of the building with access keys inside. Keys will need to be on site for the final inspection.

- Physical Address

- The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.

- The numbers used to make up the physical address shall be at least six inches in height.

- Panic Hardware

- UL 305 listed panic hardware is required on exit doors serving a room/space with an occupant load >50, also indicated on Building code summary.

- Notes

  - A final fire inspection is required. Please contact the Harnett County Planning and Inspections office to schedule this inspection. 910-893-7525, option 1.

Thank you again for submitting the plans for the new business.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Matthew Starling

Deputy Fire Marshal

910-893-0742

mstarling@harnett.org