Fire Marshal Division

September 2, 2025

Re:	The Raynor

112 S Fayetteville Avenue

Dunn, NC 28334

Dear Applicant,

Thank you for submitting the plans for The Raynor. The plans have been carefully reviewed by a qualified code enforcement official to examine for compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

Bottom of Form

- Physical Address

- The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.  Minimum size numbers shall be six inch.

- Fire Department Access

  - The fire department access shall extend to within 150 feet of all portions of the facility.

  - The fire department access road shall be of an unobstructed width of not less than 20 feet and shall have an unobstructed vertical clearance of not less the 13 feet 6 inches.

- Knox Box

  - A secure key box shall be installed on the new building that houses all keys to all the doors within the building in which the fire department would need access to in the event of an emergency.

  - The box shall be mounted not to exceed 48 – 60 inches in height.

- Fire Extinguishers

  - Fire extinguishers shall be placed in approved locations and may be field verified on final inspection.

  - The fire extinguishers provided shall have a minimum rating of 2A 10 B: C and shall not be installed higher than five feet above the finished floor.

  - Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher.

- Panic Hardware

- UL 305 listed panic hardware is required on exit doors serving a room/space with an occupant load >50, also indicated on Building code summary.

- Notes

- Plans will need to be provided for the sprinkler system, fire alarm system, and hood suppression systems.

- All inspections need to be scheduled through the Harnett County Planning Office.

Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,

Matthew Starling

Deputy Fire Marshal

910-893-0742

mstarling@harnett.org