**September 8, 2025**

**RE: SAMET Corporation**

**2983 Arrowhead Road**

**Dunn, NC 28334**

To Whom It May Concern,

Thank you for submitting the plans for the temporary trailer. The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents. There are some items that were found during the plan review process that need to be addressed before a final inspection of the updated facility can be given. These items are outlined and described below.

* **Fire Extinguishers**
* Fire extinguishers were not shown on the plans, but are required.
* The fire extinguishers provided shall have a minimum rating of 2A:10BC and shall not be installed higher than five feet above the finished floor.
* Travel distance to an extinguisher must not exceed 75 feet.
* **Emergency Lighting**
* All emergency lighting shall be in proper operating condition at the time of final inspection.
* The means of egress, including the exit discharge, shall be illuminated at all times.
* **Notes**
* A final inspection will be required upon completion of setup. Please call the Harnett County Planning and Inspections Office to schedule the inspection.

Thank you again for submitting the plans for the temporary trailer. Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings. These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office.

Again, thank you and we look forward to working with you during the construction

period!

Sincerely,



Matthew Starling

Deputy Fire Marshal

[mstarling@harnett.org](mailto:mstarling@harnett.org)

910-893-0742