[image: image1.jpg]




Fire Marshal Division
November 4, 2025
RE: 
Firehouse Subs

65 Sadler Road

Dunn, NC 28334
Application Number: FMFW2510-0016
To Whom It May Concern,
Thank you for submitting the plans for the new restaurant.  The plans have been carefully reviewed by a qualified code enforcement official to examine for full compliance with the North Carolina Fire Prevention Code and all other fire protection regulatory documents.  There are some items that were found during the plan review process that need to be addressed before a final inspection of the new facility can be given.  These items are outlined and described below.

·  Fire Extinguishers
· The fire extinguishers provided shall have a minimum rating of 2A 10B: C and shall not be installed higher than five feet above the finished floor.
· Travel distance shall not exceed 75 feet.
· In addition to the above extinguishers, a portable fire extinguisher shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher.

Bottom of Form

·  Emergency Lighting
· All emergency lighting shall be in proper operating condition at time of final inspection.

· Illumination requirements also include the exit discharge.
·  Physical Address

· The physical address of the building shall be posted in a conspicuous place so that it can be seen on approach from the road, access road, and/or parking lot.
· The numbers used to make up the physical address shall be at least six inches in height. 

· The physical address needs to be posted on the side entrance of the building also. 
· Notes
· A final fire inspection is required. Please schedule the inspection through the Harnett County Permitting Office at 910-893-7525, option 1.
Thank you again for submitting the plans for the new business.  Please review the plans and adhere to any notes and alterations that were made in addition to the original drawings.  These remarks are for the plans that were submitted and its original intent. These remarks do not apply if the original intent changes or what was submitted on the above date changes. If you have any questions, please do not hesitate to call this office

Again, thank you and we look forward to working with you during the construction period!

Sincerely,


Matthew Starling
Deputy Fire Marshal

mstarling@harnett.org
910-893-0742
